Theory

for

#### CT SAT Calculator (PSRC)

Original document:  4 June 2001. 30 Sept. 03: changed cos to sin in (8), (9), (10); RP to 1/RP in (12) and (13)

Spreadsheet originated by the IEEE PSRC committee responsible for

C37.110 "IEEE Guide for the Application of Current Transformers Used for Protective Relaying Purposes"

Person responsible for corrections or improvements - Glenn Swift  at gswift@ieee.org

##### Introduction

The spread sheet “CT Saturation Calculator” is intended to provide quick indication not only of whether or not a CT will saturate in a particular application, but also an accurate indication of the actual waveshape of the secondary current so that the degree of saturation as a function of time is apparent. Furthermore, the data is available to the user to use as input to a digital relay model, if such is available. The user can convert the data into a COMTRADE file, for example.

There are many technical papers on the subject of modeling the behavior of iron-cored current transformers used for protective relaying purposes. One of the difficulties in using an elaborate model (in any field of engineering) is in getting the parameters in a particular case in order to implement that model easily, efficiently and accurately. For example, the excitation current in the region below the knee-point is a complex combination of magnetizing, hysteresis and eddy-current components, the parameters of which are usually not known in a particular case.

It turns out (can be shown) that, if the excitation current waveform reaches into the saturated region, the part of the waveform in the below-knee-point region has negligible effect on the overall solution. This simplifies the solution greatly, with little effect on accuracy.

If errors under low current, low burden conditions are of interest, a more elaborate model must be used.

### Testing of the Model

The proof of the pudding is in the eating. Because this model is new and quite different from those in the literature, testing against real high-current laboratory results was important. To this end, two laboratory examples published in reference (1) were compared against results from this program. The agreement was very close. [Note the comment at the end of reference (1).]

In addition, the program has had widespread circulation, and to date there are two utility-user reports of agreement with previous results and no reports of disagreement.

Circuit model

The circuit model is shown in Fig. 1.

Fig. 1  Circuit model.

The symbols used in Fig.1 as well as those used in what follows and on the spread sheet are listed in the next section.

### Symbols

All units are SI: volts, amps, weber-turns, ohms, henries, radians, seconds.

i1	instantaneous primary current

IP	rms symmetrical primary fault current

Off	dc-offset magnitude (per unit)

1	system time constant

i2	instantaneous secondary current

is	instantaneous ideal secondary current

ie	instantaneous excitation current

Ie	rms excitation current

Ipk	peak excitation current

ve	instantaneous excitation voltage

Ve	rms excitation voltage

Vs	rms ‘saturation voltage’

	instantaneous flux-linkages

rem	remanence (per unit of Vs)

S	inverse of slope of Ve vs Ie curve

A	parameter of ie vs  curve

RP	factor defined as  Ie /Ipk

	radian frequency = 260

T	one period: 2 radians

Rw	winding resistance

Rb	burden resistance

Rt	Rw + Rb

Lb	burden inductance

### The Excitation Curve

The excitation characteristic of the CT is invariably a plot of secondary rms voltage versus secondary rms current, on log-log axes, as shown in Fig. 2.

For this model, only two parameters need to be extracted from the curve: S and VS .  See Fig. 3.

Fig. 2  Factory-supplied information: the excitation curve.

Fig. 3  Method of determining the parameters Vs and S

for the saturation curve used in the model.

The reason for choosing the saturation voltage, Vs ,  at the point where the excitation current is ten amps, is that this is the definition used in the standard.  For example, a  C400  CT is one in which the excitation voltage is 400 volts rms (or more) for an error current of 10 amps. Caution: in setting up a particular case, use the actual value for Vs rather than the rating value because a CT rated C400 may actually supply, for example, 423 volts at 10 amps.

In order to check the validity of ignoring the high-slope low-end of the saturation curve, two models were compared: one the model of Fig. 3, and another the model of Fig. 4. As long as the condition was at or near saturation, there was no visible difference in the saturation curves, because the below-the-knee-point currents are very small by comparison with even mild saturation currents.  The decided advantage of eliminating this region from the model is that the hysteresis and eddy current parameters are very difficult to determine. They are not included in standard data for CT’s.

### Fig. 4  Temporary test model.

### Conversion to Instantaneous Quantities

The straight line curve with slope  1/S  shown in Fig. 3 is not linear.  It is a curve defined mathematically as

logVe=1SlogIe+logVi 	(1)

where Vi is the value of Ve  for  Ie=1, that is for log Ie=0.  Removing the logs:

Ve=ViIe1S.	(2)

Remember that these are all rms quantities, presumably measured with “true-rms” voltmeters and ammeters. [A study has shown that if rms-calibrated meters were used, with either peak-sensitive or rectified-average-sensitive elements, the effect on accuracy is not substantial.]

In order to solve the differential equations implied by the circuit of Fig. 1, one needs the instantaneous    versus  ie  curve. It is postulated here that a curve defined as

ie=A⋅λS	(3)

is suitable as long as the exponent  S  is an odd integer. In order to allow  S  to be any positive number, and keep the function odd, we can use the following more general expression:

ie=A⋅sgn(λ)⋅|λ|S	(4)

where  sgn() is the sign of  . See Fig. 5 showing a sample plot of this function.

Fig. 5. Postulated instantaneous values saturation curve.

The next step is to determine the constant  A  in terms of known parameters.

First, the flux-linkages    are related to the instantaneous excitation voltage  ve  by Faraday’s law (The error due to ignoring  Rw  here is very small - less than the measurement errors involved in determining the  Ve  vs  Ie  curve):

ve=dλdt	(5)

The excitation curve is found using sinusoidal voltage, which implies that the flux-linkages are also sinusoidal:

ve=2Vecos(ωt), and	(6)

λ=vedt=2Vecos(ωt)dt=2Ve1ωsin(ωt).	(7)

The excitation current is non-sinusoidal, since it is an Sth order function of   :

ie=AλS=A2Veωsin(ωt)S=A2VeωSsinS(ωt)	(8)

The rms value of this current is, by definition:

Ie=12π02πie2dt=12π02πA22Veω2Ssin2S(ωt)dt

=A2VeωS12π02πsin2S(ωt)dt	(9)

Next, we define the ratio of rms-value-to-peak-value of the excitation current as RP :

RP=rmspeak .

For a sinusoid RF=0.7071, and for ie  RP is given by

RP=12π02πIpk2sin2S(ωt)dtIpk=12π02πsin2S(ωt)dt	(10)

The above definite integral, (and hence RP) can best be evaluated using numerical integration, and in fact this is done directly on the spread sheet - using trapezoidal integration - for the particular  S  entered by the user.

Fig. 6 illustrates the difference between rms/peak for a sinusoid and rms/peak for the assumed excitation current waveform: the form factor  RP  gets smaller as the value of  S  increases.

Fig.6  Comparison of the rms/peak relationship for two waveshapes.

Left: excitation voltage or flux-linkages.  Right: excitation current.

Substituting this result into equation (8), yields

Ie=A2VeωSRP	(11)

But we know that when  Ie=10 , Ve=Vs.  Substituting,

10=A2VsωSRP.

Solving for A:

A=10ωS2VsS1RP.	(12)

Equation (4) becomes, therefore, the fundamental  ie vs  relationship:

ie=sgn(λ)10ωS2VsS1RP⋅|λ|S               as illustrated in Fig. 5.	(13)

### Solution of Circuit Model

The circuit of Fig. 1 is solved simply by writing Kirchhoff’s Voltage Law around the right-hand loop:

ve−(is−ie)⋅Rt−Lbddtis−ie=0	(14)

The ‘forcing function’ and its derivative are:

is=i1N=2⋅IpNOff⋅e−tTau1−cos(ωt−cos−1Off)	(15)

disdt=2⋅IpN−OffTau1⋅e−tTau1+ω⋅sin(ωt−cos−1Off)	(16)

Note that

diedt=diedλ⋅dλdt	(17)

and

diedλ=A⋅S⋅|λ|S−1.	(18)

Finally, with substitutions and manipulation, equation (14) is re-written as:

dλdt⋅1+Lb⋅A⋅S⋅|λ|S−1=−Rtie+Rtis+Lbdisdt	(18)

dependent variable	forcing function

This first-order nonlinear differential equation is solved for  t  using standard numerical analysis techniques, such as trapezoidal integration, Runge-Kutta integration, or simple step increments. The latter is used in the spread sheet program, for simplicity, since the accuracy is sufficient for this application.

Then the excitation(error) current  ie  is given by equation (3), and the actual secondary current - the goal of this exercise - by

i2=is−ie	(19)

### Remanence

With the single-valued saturation curve assumed here, conventional remanence is not possible because non-zero  cannot occur for zero ie .  However, remanence can be approximated very closely by simply assuming that the initial excitation current is non-zero. A quite small initial excitation current will accomplish this, even for a large remanence. For convenience,  rem  is expressed in per unit of  Vs  since the “knee-point” itself is not defined in this model.  See Fig. 7. In order to specify  rem accurately,  x   must be specified no greater than  Vknee  in Fig. 7. In other words, if  Vknee  is 80% of  VS  then the value of  rem  cannot exceed 0.8 per unit.

### Fig. 7  Definition of per unit remanence used in this model.

### References

(1) Tziouvaras, D.A., et al, Mathematical Models for Current, Voltage, and Coupling Capacitor Voltage Transformers, Working Group C5 of PSRC, IEEE Trans. on Power Delivery, Jan 2000, pp. 62-72. (Note that there is an error in figures 4a and 5a of this paper: there was actually non-zero remanence for this case, as confirmed with the authors.)