## Electrical
BETA - please double check calculations independently
Tigo TS4 PV Module Compatibility Calculator
Note: this tab has been sized to print or save as pdf as 1 page for your records
INPUTS
Enter the values unique to your site in the green cells. Additional instructions are provided to the right of some cells.
Input STC characteristics (from module datasheet)
Pmax | 710 | W
Vmp | 40.9 | V
Imp | 17.36 | A
Voc | 49 | V
Isc | 18.4 | A
Temperature coefficient (Pmax) | -0.29 | %/°C | Input negative value
Temperature coefficient (Voc) | -0.24 | %/°C | Input negative value
Temperature coefficient (Isc) | 0.04 | %/°C | Input positive value
Input environmental conditions (based on location)
Bifacial gain expected | 0 | %
Lowest recorded temperature | -4 | °C
Average hottest temperature | 35 | °C
Irradiance coefficient | 1 | # [1-1.4]
Required certification | IEC |  | Choose from dropdown
RESULTS
The table below indicates the TS4's that are compatible (YES) or not (NO) based on the inputs provided
Compatible products | Compatible? | Power (W) | Imp | Isc | Max input voltage | Min input voltage | Available
TS4-A-O 700W | NO | 700 | 15 | 20 | 80 | 16 | IEC
TS4-A-S 700W | NO | 700 | 15 | 20 | 80 | 16 | UL/IEC
TS4-A-F 20A | NO | 700 | 15 | 20 | 80 | 16 | UL/IEC
TS4-A-F 25A | NO | 700 | 20 | 25 | 80 | 16 | UL/IEC
TS4-A-2F 20A | NO | 500 | 15 | 20 | 80 | 16 | UL/IEC
TS4-A-2F 25A | NO | 700 | 20 | 25 | 80 | 16 | UL/IEC
TS4-A-O 22A | NO | 725 | 16 | 22 | 80 | 12 | UL
TS4-A-S 22A | NO | 725 | 16 | 22 | 80 | 12 | UL
TS4-A-F 22A | NO | 725 | 16 | 22 | 80 | 12 | UL
TS4-X-O | YES | 800 | 20 | 25 | 80 | 12 | UL/IEC
TS4-X-S | YES | 800 | 20 | 25 | 80 | 12 | UL/IEC
TS4-X-F | YES | 800 | 20 | 25 | 80 | 12 | UL/IEC
CALCULATIONS
These calculations are based on the inputs provided and are for reference only
Calc max values | Values | Units | Notes
Voltage min | 39.7139 | V | Corrected to high temp
Voltage max | 52.4104 | V | Corrected to low temp
Power max | 710 | W | Corrected to irradiance and bifacial gain
Isc max | 18.4736 | A | Corrected to irradiance, bifacial gain and high temp
Imp max | 17.4294 | A | Corrected to irradiance, bifacial gain and high temp
Power max bifacial only | 710 | W | Corrected to bifacial gain
Isc max bifacial only | 18.4 | A | Corrected to bifacial gain
Imp max bifacial only | 17.36 | A | Corrected to bifacial gain
TS4 data
| TS4-A-O 700W | TS4-A-S 700W | TS4-A-F 20A | TS4-A-F 25A | TS4-A-2F 20A | TS4-A-2F 25A | TS4-A-O 22A | TS4-A-S 22A | TS4-A-F 22A | TS4-X-O | TS4-X-S | TS4-X-F
Power (per input) | 700 | 700 | 700 | 700 | 500 | 700 | 725 | 725 | 725 | 800 | 800 | 800 | UL | IEC
Imp | 15 | 15 | 15 | 20 | 15 | 20 | 16 | 16 | 16 | 20 | 20 | 20
Isc | 20 | 20 | 20 | 25 | 20 | 25 | 22 | 22 | 22 | 25 | 25 | 25
Max input voltage | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
Min input voltage | 16 | 16 | 16 | 16 | 16 | 16 | 12 | 12 | 12 | 12 | 12 | 12
Availale | IEC | UL/IEC | UL/IEC | UL/IEC | UL/IEC | UL/IEC | UL | UL | UL | UL/IEC | UL/IEC | UL/IEC
BETA version 1.1 | PN: TIG-FRM-0008 | [5 empty] | 2025-08-14

## Cable-length
BETA - please double check calculations independently
Tigo TS4 Cable Length Calculator
Note: this tab has been sized to print or save as pdf as 1 page for your records
Enter the module parameters in the light green cells |  |  |  |  | SELECTED CONFIGURATION
if this doesn't look correct, adjust the inputs in the 'module specs' section
INPUTS |  |  |  |  | #VALUE!
Module specs
Module width (mm) | 1134 | width = shorter side
Module length (mm) | 2279 | length = longer side
Module orientation | Portrait | see image on right to validate
Junction box type | Split
Junction box location | Top
Junction box lead length (mm) | 600
RESULTS
TS4 lead length options | Input (mm) | Output (mm) | Compatible?
TS4-X-O/S/F | 600 | 1200 | YES
TS4-X-O/S/F | 1200 | 2000 | YES
TS4-A-O/S/F | 1200 | 2000 | YES
TS4-A-O/S/F | 120 | 1200 | NO
TS4-A-O/S/F | 620 | 1200 | YES
Minimum lead length requirements
Min input length (mm) | 352.07
Min output length (mm) | 617 |  |  |  | Installer / EPC / Designer required to validate that system lengths comply with bend radius, desired cable runs, and design requirements.
BETA version 1.1 | PN: TIG-FRM-0008 | [8 empty] | 2025-08-14
INTERMEDIARY CALCULATIONS
Unique string | PortraitSplitTop
Horizontal length (1 module) | 1134
Vertical length (1 module) | 2279
Notes
- we try to put the TS4 in the middle of the module
- Outputs must be at least 1/2 + 50mm of the width of the module
- If it's in portrait, need 100mm to accommodate the bend radius
- Inputs have to take into account the module leads and the width
- input length (+50mm) + lead length must be greater than 1/2 the length of the total module
- Junction box locations are almost always in the horizontal middle.
- Split junction boxes are common for commercial. Typically 200mm in from the module frame
- RECOMMENDED MINIMUM BENDING RADIUS SINGLE AND MULTIPLE CONDUCTORS (NEC 300.34) MULTIPLE OF CABLE O.D. Where D = Overall Cable Diameter *12 times individual shielded conductor diameter or 7 times overall cable diameter, whichever is greater.
CALCULATOR ASSUMPTIONS
Bend Radius (mm) | 75
[6 empty] | OUTPUT calcs |  |  | INPUT calcs
Configuration # | Module orientation | Junction box | Junction Box locations | String | Image | % of horizontal edge length | + length adder (mm) | Min output length (mm) | % of vertical edge length | + length adder (mm) | - % of input lead length | Min input length (mm)
1 | Portrait | Single | Top | PortraitSingleTop | #VALUE! | 50% | 50 | 617 | 33% | 50 | 75% | 352.07
2 | Portrait | Single | Middle | PortraitSingleMiddle | #VALUE! | 50% | 50 | 617 | 50% | 50 | 75% | 739.5
3 | Portrait | Single | Bottom | PortraitSingleBottom | #VALUE! | 50% | 100 | 667 | 50% | 100 | 75% | 789.5
4 | Landscape | Single | Top | LandscapeSingleTop | #VALUE! | 50% | 50 | 617 | 75% | 100 | 75% | 1359.25
5 | Landscape | Single | Middle | LandscapeSingleMiddle | #VALUE! | 50% | 50 | 617 | 50% | 50 | 75% | 739.5
6 | Landscape | Single | Bottom | LandscapeSingleBottom | #VALUE! | 50% | 50 | 617 | 75% | 100 | 75% | 1359.25
7 | Portrait | Split | Top | PortraitSplitTop | #VALUE! | 50% | 50 | 617 | 33% | 50 | 75% | 352.07
8 | Portrait | Split | Middle | PortraitSplitMiddle | #VALUE! | 50% | 50 | 617 | 50% | 100 | 75% | 789.5
9 | Portrait | Split | Bottom | PortraitSplitBottom | #VALUE! | 50% | 100 | 667 | 50% | 100 | 75% | 789.5
10 | Landscape | Split | Top | LandscapeSplitTop | #VALUE! | 50% | 50 | 617 | 75% | 100 | 75% | 1359.25
11 | Landscape | Split | Middle | LandscapeSplitMiddle | #VALUE! | 50% | 50 | 617 | 75% | 50 | 75% | 1309.25
12 | Landscape | Split | Bottom | LandscapeSplitBottom | #VALUE! | 50% | 50 | 617 | 75% | 100 | 75% | 1359.25
Drop Down options
| Module orientation | Junction box | Junction Box locations
| Portrait | Single | Top
| Landscape | Split | Middle
Bottom