## Solar Sizing
Module Data (STC) |  |  |  |  | Entry Fields |  |  | Step 1: Enter Module & Temps
Open Circuit Voltage | Voc | V | 50.45 | Positive only
Maximum Power Voltage | Vmp | V | 49.4 | Positive only
Short Circuit Current | Isc | A | 8.84 | 16.9 A max
Maximum Power Current | Imp | A | 8.3 | 13.5 A max
Temp. Coeff. of Voc | βvoc | %/⁰C | -0.24% | Values have to be negative; never less than -1%
Temp. Coeff. Of Max Power | βmp | %/⁰C | -0.24% | Values have to be negative; never less than -1%
Maximum Power | Pmax | W | 410 | 700 W max
Location Temperature |  |  |  | Temp Lookup
Degrees |  |  | C | Choose C or F
Lowest Temperature |  |  | 0
Highest Temperature |  |  | 40
System Info
System Voltage |  |  | 240
System Location |  |  | Rooftop | Default
Module |  |  | Inverter
STC Temp | 25 | 25 | Min V | 80 | volts |  | 0
Temp below STC | 25 | deg | Max V | 550 | volts |  | 40
Temp Coeff Change | 0.06 |  | Max Isc | 13.5 | amps
Voltage Increase | 3.027 | v | 3.8 | 3800 | w
Voltage at lowest Temp | 53.477 | v | 7.6 | 7600 | w
|  |  | 11.4 | 11400 | w
[5 empty] | Efficiency | Min String Length 3.8 | 4
Min Voltage | 44.6576 | v | Max String Length 3.8 | 8 | 0.97 | Min String Length 7.6 | 5
|  |  | Max Sting Length 7.6 | 10 | 0.975 | Min String Length 11.4 | 5
System Calcs |  |  | Max String Length 11.4 | 10 | 0.98
DC Wattage | 8200
MPPTs Required | 2 | 3
MPPTs Required / Inverter | 3.8 | 2 | 0 | 0
| 7.6 | 3 | 0 | -1
| 11.4 | 4 | -1 | -1
Max Modules / inverter | 3.8 | 16 | 0 | 4 | 48
| 7.6 | 30 | 0 | -10 | 90
| 11.4 | 40 | -10 | -10
System Size |  |  |  |  | Size Allowed / Inverter |  |  | Step 2:
Size Wanted / Existing |  |  | 20 |  | Min | Max |  | Enter in System Size Desired
Units |  |  | Module Qty |  | 4 | 120 | Modules
[5 empty] | 1.64 | 49.2 | kW
Max DC/AC Ratio Wanted |  |  | 200 | %
Module Voltage (Adjusted) |  | String Lengths |  |  |  | Actual Array Characteristics |  | ** Max string size rounds down
Voc @ Min. Temp |  | Inverter Size | Min | Max |  | 20 | Module Qty | ** Will cause Actual DC / AC Ratio to be lower than limit
53.477 | v | 3.8 | 4 | 8 |  | 8.2 | System Size (kW) | ** Min string size rounds up
Vmp @ Max. Temp |  | 7.6 | 5 | 10
44.6576 | v | 11.4 | 5 | 10
| Qty. | [6 empty] | Step 3: System Configuration
3.8 Inverters | 0 | [6 empty] | ** OR will appear next to the quantity if upsizing the inverter is desired
Inverter 1: MPPT Configuration |  |  | Inverter 2: MPPT Configuration |  |  | Inverter 3: MPPT Configuration
Mppt # | Module Qty |  | Mppt # | Module Qty |  | Mppt # | Module Qty
1 | - |  | 1 | - |  | 1 | -
2 | - |  | 2 | - |  | 2 | -
DC/AC Ratio | 0% |  | DC/AC Ratio | 0% |  | DC/AC Ratio | 0%
7.6 Inverters | Qty.
1
Inverter 1: MPPT Configuration |  |  | Inverter 2: MPPT Configuration |  |  | Inverter 3: MPPT Configuration
Mppt # | Module Qty |  | Mppt # | Module Qty |  | Mppt # | Module Qty
1 | 10 |  | 1 | - |  | 1 | -
2 | 10 |  | 2 | - |  | 2 | -
3 | 0 |  | 3 | - |  | 3 | -
DC/AC Ratio | 110.7% |  | DC/AC Ratio | 0% |  | DC/AC Ratio | 0%
11.4 Inverters | Qty.
OR | 1
Inverter 1: MPPT Configuration |  |  | Inverter 2: MPPT Configuration |  |  | Inverter 3: MPPT Configuration
Mppt # | Module Qty |  | Mppt # | Module Qty |  | Mppt # | Module Qty
1 | 10 |  | 1 | - |  | 1 | -
2 | 10 |  | 2 | - |  | 2 | -
3 | 0 |  | 3 | - |  | 3 | -
4 | - |  | 4 | - |  | 4 | -
DC/AC Ratio | 73.4% |  | DC/AC Ratio | 0% |  | DC/AC Ratio | 0%
Terms & Conditions
THE USER OF THIS TOOL HAS ACKNOWLEDGED:
The EI Inverter & String Sizing Tool is offered free of charge as a guide only.
It is the responsibility of the system design engineer to ensure that the PV module characteristics and system settings are appropriate for the system being considered.
The user agreees to use this EI Inverter & String Sizer Tool spreadsheet at their own risk and with the knowledge that Tigo Energy will not be liable to the user for any damages, injury or death as a result of use of the EI Inverter & String Sizing Tool.
PN: 002-00198-00 ¦ version 1.0

## Battery Sizing
Tigo Battery Backup Tool (US Inverters and Batteries)
Toggle on and off different loads with the "Yes" or "No" selections under Include.
To turn off whole tiers, see rows 44-46.
<< Editable cells have a green outline.
Tier | Item | Rating (W) | # | Hours | Power (W) | Energy (Wh) | Include
Tier 1 | Refrigerator | 400 | 3 | 7 | 1200 | 2800 | Yes | Battery Power (kW) and Energy (kWh) available
| WiFi Router + modem | 20 | 1 | 24 | 20 | 480 | Yes | Inverter size (kW) | # of EI Batteries |  |  | Max PV capacity (kW) | Breaker space (A)
| Laptop | 78 | 3 | 9 | 234 | 702 | Yes | Inverter Size | 1 | 2 | 4
| Monitor | 10 | 2 | 9 | 20 | 90 | Yes |  | Max Continuous Power (kW)
| Device Charger | 10 | 3 | 4 | 30 | 40 | Yes | 3.8 | 3.8 | 3.8 | 3.8 | 7.6 | 20
| TV & Cable | 200 | 1 | 4 | 200 | 800 | Yes | 7.6 | 5 | 7.6 | 7.6 | 15.2 | 40
| Game console | 100 | 1 | 3 | 100 | 300 | Yes | 11.4 | 5 | 10 | 10 | 22.8 | 60
| Kitchen lights | 8 | 10 | 6 | 80 | 48 | Yes |  | Total Usable Energy (kWh)
| Bathroom lights | 8 | 20 | 4 | 160 | 32 | Yes | ALL | 9 | 18 | 36
| Bedroom lights | 8 | 20 | 6 | 160 | 48 | Yes
| Garage door | 400 | 1 | 0.1 | 400 | 40 | Yes
| Microwave | 600 | 1 | 0.15 | 600 | 90 | Yes | Backup: Power (% of max) and Energy (days)
| Ceiling Fan | 65 | 1 | 5 | 65 | 325 | Yes | Inverter size (kW) | # of EI Batteries |  |  | Max PV capacity (kW) | Breaker space (A)
| Coffee Maker | 600 | 1 | 0.15 | 600 | 90 | Yes | Inverter Size | 1 | 2 | 4
| Tier 1 Total |  |  |  | 3869 | 5885 |  |  | % of Power Required
[8 empty] | 3.8 | 67.03% | 67.03% | 67.03% | 7.6 | 20
Tier 2 | Sump Pump | 400 | 1 | 6 | 400 | 2400 | No | 7.6 | 88.2% | 134.1% | 134.1% | 15.2 | 40
| Dishwasher | 1200 | 1 | 3 | 1200 | 3600 | Yes | 11.4 | 88.2% | 176.4% | 176.4% | 22.8 | 60
| Air Conditioner (Window) | 600 | 1 | 8 | 600 | 4800 | Yes |  | Backup Energy Available
| Furnace Blower Motor | 600 | 1 | 6 | 600 | 3600 | No | # hours | 15.1208 | 30.2415 | 60.483
| Washing Machine | 500 | 1 | 6 | 500 | 3000 | No | # days | 0.63003 | 1.2601 | 2.5201
| Tier 2 Total |  |  |  | 1800 | 8400
Tier 3 | AC (1 ton) | 1000 | 1 | 8 | 1000 | 8000 | No | Backup energy available with solar production (% of daily energy covered)
| AC (2 ton) | 2000 | 1 | 8 | 2000 | 16000 | Yes | System Size (kW): | 10
| Minisplit - 1 zone | 700 | 1 | 8 | 700 | 5600 | No
| Minisplit - 4 zone | 2800 | 1 | 8 | 2800 | 22400 | No | Capacity Factor (%) | # of EI Batteries |  |  | Daily PV Energy (kWh) | Note
| Heater - electric | 1500 | 1 | 7 | 1500 | 10500 | Yes |  | 1 | 2 | 4
| Heater - heat pump | 5000 | 1 | 7 | 5000 | 35000 | No |  | % of Daily Energy Covered |  |  |  | Capacity factor: ratio of energy output to PV system size. Sunny summer CA day: ~25%. Cloudy, stormy: <5%.
| Water Heater - electric | 4500 | 1 | 3 | 4500 | 13500 | No | 0% | 63% | 126% | 252% | 0
| Stove - electric | 5000 | 1 | 2 | 5000 | 10000 | Yes | 5% | 147% | 210% | 336% | 12
| Clothes Dryer | 4000 | 1 | 2 | 4000 | 8000 | No | 10% | 231% | 294% | 420% | 24
| Well Pump | 1000 | 1 | 6 | 1000 | 6000 | No | 15% | 315% | 378% | 504% | 36
| Dishwasher | 1200 | 1 | 3 | 1200 | 3600 | No | 20% | 399% | 462% | 588% | 48
| Electric Vehicle Charger | 7200 | 1 | 10 | 7200 | 72000 | No | 25% | 483% | 546% | 672% | 60
| Tier 3 Total |  |  |  | 8500 | 36500
Battery Assumptions - Power (kW) and Usable Energy (kWh)
Totals | Tier 1 Total |  |  |  | 3869 | 5885 | Yes |  | # of EI Batteries |  |  |  | Selections
| Tier 2 Total |  |  |  | 1800 | 8400 | Yes |  | 1 | 2 | 4 |  | Yes
| Tier 3 Total |  |  |  | 8500 | 36500 | No | Power (kW) | 5 | 10 | 10 |  | No
| Grand Total |  |  |  | 5669 | 14285 |  | Energy (kWh) | 9 | 18 | 36
PN: 002-00198-00 ¦ version 1.0

## Battery Sizing OLD (hidden)
Backup System Requirements | [8 empty] | Step 1:
Backup Hours Needed Per Day |  |  | Hours | 12 | Cannot be greater than 24 |  |  |  | Enter Backup Load Requirements
Minimum Battery Reserve |  |  | % | 10% | Default to 10%, Max of 50%
Backup Load Calculations
Item | Power (Cont.) |  | Power (Surge) |  | Hrs per Day | Qty | Item Consumption
Lights | 20 | W | 35 | W | 10.5 | 100 | 10500 | kWh
None | 0 | W | 0 | W | 0 | 1 | 0 | kWh
None | 0 | W | 0 | W | 0 | 1 | 0 | kWh
None | 0 | W | 0 | W | 0 | 1 | 0 | kWh
None | 0 | W | 0 | W | 0 | 1 | 0 | kWh
None | 0 | W | 0 | W | 0 | 1 | 0 | kWh
None | 0 | W | 0 | W | 0 | 1 | 0 | kWh
None | 0 | W | 0 | W | 0 | 1 | 0 | kWh
None | 0 | W | 0 | W | 0 | 1 | 0 | kWh
None | 0 | W | 0 | W | 0 | 1 | 0 | kWh
Total: | 20 | Watts | 35 | Watts |  |  | 10500 | kWh
Total Power Needed
2000 | W
Total Surge Power Needed
3500 | W
Total Consumption Needed |  | Battery Reserve Energy Needed |  |  | Total Energy Needed
11026.26 | Wh | 1980 | Wh |  | 13006.26 | Wh
Battery Qty Needed |  | Min. EI Inverter Needed |  |  |  | Battery Capacity |  |  | Step 2:
TSB-10-XX |  | 3.8 | 7.6 | 11.4 |  | 20 | kWh |  | Calculate Battery Size Required
2
2
2 |  | 1 | 0 | 0 |  |  |  |  | kWh Check
Power/Inverter Qty Check
Battery Backup (No Solar) |  |  | Self-Consumption
Autonomy Expected (h) | 35.9827 | hrs | Avg. Daily Depth of Discharge |  |  | 34.97%
Worse Case (h) | 15.4023 | hrs

## Battery + Solar (hidden)
Module Data (STC) |  |  |  | Input Cell | [6 empty] | Step 1:
Open Circuit Voltage | Voc | V | 40 | Positive only | [6 empty] | Enter Module & Temp Info
Maximum Power Voltage | Vmp | V | 30 | Positive only
Short Circuit Current | Isc | A | 13 | 16.9 A max
Maximum Power Current | Imp | A | 11 | 13.5 A max
Temp. Coeff. of Voc | βvoc | %/⁰C | -0.27% | Values have to be negative; never less than -1%
Temp. Coeff. of Max Power | βmp | %/⁰C | -0.32% | Values have to be negative; never less than -1%
Maximum Power | Pmax | W | 300 | 700 W max
Location Temperature |  |  |  | Temp Lookup
Degrees |  |  | C | Choose C or F
Lowest Temperature |  |  | -10
Highest Temperature |  |  | 55
System Info
System Voltage |  |  | 240 | V
System Location |  |  | Rooftop
Backup System Requirements | [10 empty] | Step 2:
Backup Hours / Day Needed |  |  | Hours | 18 | Cannot be greater than 24 | [5 empty] | Enter Backup Load Requirements
Minimum Battery Reserve |  |  | % | 10% | Minimum of 10%, Max of 50% | [5 empty] | Pull Temp Data here
Backup Load Calculations
Item | Power |  | Surge |  | Hrs per Day | Qty | Item Consumption
Lights | 20 | W | 20 | W | 10.5 | 50 | 7875 | kWh
Garage Door Opener | 650 | W | 200 | W | 0.05 | 1 | 24.375 | kWh
Microwave | 1200 | W | 200 | W | 0.6 | 5 | 2700 | kWh
Laptop / PC | 100 | W | 100 | W | 6.3 | 1 | 472.5 | kWh
None | 0 | W | 0 | W | 0 | 1 | 0 | kWh
None | 0 | W | 0 | W | 0 | 1 | 0 | kWh
None | 0 | W | 0 | W | 0 | 1 | 0 | kWh
None | 0 | W | 0 | W | 0 | 1 | 0 | kWh
None | 0 | W | 0 | W | 0 | 1 | 0 | kWh
None | 0 | W | 0 | W | 0 | 1 | 0 | kWh
None | 0 | W | 0 | W | 0 | 1 | 0 | kWh
None | 0 | W | 0 | W | 0 | 1 | 0 | kWh
Wifi Router | 10 | W | 10 | W | 10 | 1 | 75 | kWh
Total: | 1980 | Watts | 530 | Watts |  |  | 11146.875 | kWh
[12 empty] | A46 Old Equation | A45 Old Equation
Total Power Needed | [11 empty] | 2 | -1
7760 | W
Total Surge Power Needed
2310 | W
Total Consumption Needed |  | Battery Reserve Energy Needed |  |  | Total Energy Needed
11705.4788 | Wh | 1980 | Wh |  | 13685.4788 | Wh
Battery Qty Needed |  | Min. EI Battery Inverter Needed |  |  |  | Max Solar Allowed |  |  |  |  | Step 3:
TSB-10-XX |  | 3.8 | 7.6 | 11.4 |  | 52 | Modules |  |  |  | Calculate Battery Size Required
2 | [10 empty] | kWh Check
2 | [10 empty] | Inverter Qty Check
2 |  | 0 | 0 | 1 |  | 15.6 | kW DC |  |  |  | Specify Largest System Size Possible
[6 empty] | 11.4 | kW AC |  |  |  | ** Attach batteries to largest inverter
Max Battery Discharge | 10 | kW |  |  |  | 136.8% | DC/AC Ratio
Battery Capacity | 20 | kWh
NREL API - Future | API Key | WHGYFoNh0lxs0n0b8yZdr3vlI9PnFOC5xKNeW65z |  |  |  |  | URL: | https://developer.nrel.gov/api/pvwatts/v6.json?api_key=WHGYFoNh0lxs0n0b8yZdr3vlI9PnFOC5xKNeW65z&address=96161&tilt=20&azimuth=180&system_capacity=1&array_type=1&module_type=1&losses=12.4097806403839&radius=0
System Size | 1 | kW | Best Avg Prod / Day | 5.4255 | kWh |  |  |  |  | &system_capacity=1 | Step 4:
Tilt | 20 | Deg | Worse Case Prod / Day | 3.4377 | kWh |  |  |  |  | &tilt=20 | Enter in Solar Array Information
Azimuth | 180 | Deg | [7 empty] | &azimuth=180 | Existing or Potential
Zip Code | 96161 | [8 empty] | &address=96161
Tigo MLPE | O/H
Daily Prod
System Production |  |  | kWh
| Monthly | AC | 1 | 5.7 | 11.4 | kW DC | Losses | Non-Opt | Optimizer
Jan | 110.45 | kWh | 3.5629 | 20.3085 | 40.6171 | kWh | Soiling | 2% | 2%
Feb | 113.88 | kWh | 4.0671 | 23.1827 | 46.3654 | kWh | Shading | 3% | 3%
Mar | 148.22 | kWh | 4.7813 | 27.2534 | 54.5067 | kWh | Snow | 0% | 0%
Apr | 153.86 | kWh | 5.1287 | 29.2334 | 58.4668 | kWh | Mismatch | 2% | 0.1%
May | 168.19 | kWh | 5.4255 | 30.9253 | 61.8505 | kWh | Wiring | 2% | 2%
June | 158.21 | kWh | 5.2737 | 30.0599 | 60.1198 | kWh | Connections | 0.5% | 0.5%
July | 165.71 | kWh | 5.3455 | 30.4693 | 60.9385 | kWh | Light-Induced Degradation | 1.5% | 1.5%
Aug | 163.99 | kWh | 5.29 | 30.153 | 60.306 | kWh | Nameplate Rating | 1% | 1%
Sept | 146.22 | kWh | 4.874 | 27.7818 | 55.5636 | kWh | Age | 0% | 0%
Oct | 131.81 | kWh | 4.2519 | 24.236 | 48.4721 | kWh | Availability | 3% | 3%
Nov | 115.32 | kWh | 3.844 | 21.9108 | 43.8216 | kWh
Dec | 106.57 | kWh | 3.4377 | 19.5951 | 39.1903 | kWh | System Total: | 14.08% | 12.41%
|  | Max | 5.4255 | 30.9253 | 61.8505 | kWh |  | 14.0757 | 12.4098
|  | Min | 3.4377 | 19.5951 | 39.1903 | kWh |  | 12.4098
Battery Backup (hours) | PV Impact (hrs) | [9 empty] | Step 5:
| No PV | 1 | 5.7 | 11.4 | DC | [5 empty] | Backup w/ Solar Calculations
Autonomy Expected (h) - Summer | 34.1968 | 56.7 | indefinite | indefinite | [6 empty] | Could be more intelligent here
Autonomy Expected (h) - Winter |  | 45.7 | indefinite | indefinite | [6 empty] | Genability
Worse Case (h) | 2.2471
Self-Consumption Daily (hours)
% Energy Consumed outside of PV Window |  |  | 30%
Avg. Daily Depth of Charge |  |  | 79.47%
System Size |  |  |  |  | System Size | [5 empty] | Step 4:
Size Wanted / Existing |  |  | 52 |  | 52 | Module Qty |  |  |  |  | Solar System Size Wanted
Unit |  |  | Module Qty |  | 15.6 | kW DC
Max DC/AC Ratio |  |  | 200 | %
Module |  |  | Inverter
STC Temp | 25 | 25 | Min V | 100 | volts |  | -10
Temp below STC | 35 | deg | Max V | 600 | volts |  | 55
Temp Coeff Change | 0.0945 |  | Max Isc | 13.5 | amps
Voltage Increase | 3.78 | v | 3.8 | 3800 | w
Voltage at lowest Temp | 43.78 | v | 7.6 | 7600 | w
|  |  | 11.4 | 11400 | w
|  |  | Minimum String Length | 5
Min Voltage | 24.72 | v | Max String Length 3.8 | 6
|  |  | Max Sting Length 7.6 | 13
System Calcs |  |  | Max String Length 11.4 | 13
DC Wattage | 15600
MPPTs Required | 6
3.8 String Lengths |  |  | 7.6 String Lengths |  |  | 11.4 String Lengths |  |  |  |  | Step 5:
Min | Max |  | Min | Max |  | Min | Max |  |  |  | Solar Configuration
5 | 6 |  | 5 | 13 |  | 5 | 13
Qty.
3.8 Inverters | 0
Inverter 1: MPPT Configuration
Mppt # | Module Qty
1 | -
2 | -
DC/AC Ratio | 0%
Qty.
7.6 Inverters | 2
Inverter 1: MPPT Configuration |  |  | Inverter 2: MPPT Configuration |  |  | Inverter 3: MPPT Configuration
Mppt # | Module Qty |  | Mppt # | Module Qty |  | Mppt # | Module Qty
1 | 8 |  | 1 | 9 |  | 1 | -
2 | 8 |  | 2 | 9 |  | 2 | -
3 | 9 |  | 3 | 9 |  | 3 | -
DC/AC Ratio | 98.68% |  | DC/AC Ratio | 106.6% |  | DC/AC Ratio | 0%
11.4 Inverters | Qty.
0
Inverter 1: MPPT Configuration |  |  | Inverter 2: MPPT Configuration |  |  | Inverter 3: MPPT Configuration
Mppt # | Module Qty |  | Mppt # | Module Qty |  | Mppt # | Module Qty
1 | - |  | 1 | - |  | 1 | -
2 | - |  | 2 | - |  | 2 | -
3 | - |  | 3 | - |  | 3 | -
4 | - |  | 4 | - |  | 4 | -
DC/AC Ratio | 0% |  | DC/AC Ratio | 0% |  | DC/AC Ratio | 0%

## Ref Solar (hidden)
Grid Voltage | System Sizing | Degrees | Inverter Standby Power |  |  | Optimizer | Type | 3.8 Eff. |  | 7.6 Eff. |  | 11.4 Eff.
240 | kW | C | 50 | W |  | O/H | Rooftop | 97% | 240 | 97.5% | 240 | 98% | 240
208 | Module Qty | F |  |  |  | F/2F/M/S | Ground Mount | 97% | 208 | 97% | 208 | 97.5% | 208
|  |  |  | Qty | [5 empty] | Module Quantities / MPPT
1-Phase | Modules | MPPTs Req. | 3.8 | 7.6 | 11.4 | ID |  |  | MPPTs | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| 8 | 1 | 1 | 0 | 0 | 1 |  |  | 1 | 20
| 16 | 2 | 1 | 0 | 0 | 2 |  |  | 2 | 10 | 10
| 20 | 2 | 0 | 1 | 0 | 3 |  |  | 3 | 6 | 7 | 7
| 30 | 3 | 0 | 1 | 0 | 4 |  |  | 4 | 5 | 5 | 5 | 5
| 40 | 4 | 0 | 0 | 1 | 5 |  |  | 5 | 4 | 4 | 4 | 4 | 4
| 50 | 5 | 0 | 2 | 0 | 6 |  |  | 6 | 3 | 3 | 3 | 3 | 4 | 4
| 60 | 6 | 0 | 2 | 0 | 7 |  |  | 7 | 2 | 3 | 3 | 3 | 3 | 3 | 3
| 80 | 8 | 0 | 0 | 2 | 9 |  |  | 8 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3
| 120 | 12 | 0 | 0 | 3 | 13 |  |  | 9 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3
[9 empty] | 10 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
[9 empty] | 11 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
3-Phase | Modules | MPPTs Req. | 3.8 | 7.6 | 11.4 | ID |  |  | 12 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| 24 | 3 | 3 | 0 | 0 | 1
| 32 | 4 | 3 | 0 | 0 |  |  | Inverter 2 | MPPTs | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| 40 | 5 | 3 | 0 | 0 |  |  | 3-phase | 1 | 0
| 48 | 6 | 3 | 0 | 0 | 2 |  |  | 2 | 0 | 0
| 60 | 6 | 0 | 3 | 0 |  |  |  | 3 | 0 | 0 | 0
| 70 | 7 | 0 | 3 | 0 |  |  |  | 4 | 0 | 0 | 0 | 0
| 80 | 8 | 0 | 3 | 0 |  |  |  | 5 | 0 | 0 | 0 | 0 | 0
| 90 | 9 | 0 | 3 | 0 | 4 |  |  | 6 | 0 | 0 | 0 | 0 | 0 | 0
| 90 | 9 | 0 | 0 | 3 |  |  |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 100 | 10 | 0 | 0 | 3 |  |  |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 110 | 11 | 0 | 0 | 3 |  |  |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 120 | 12 | 0 | 0 | 3 | 6 |  |  | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 12 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1
[8 empty] | Inverter 3 | MPPTs | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
[8 empty] | 3-phase | 1 | 0
[9 empty] | 2 | 0 | 0
[9 empty] | 3 | 0 | 0 | 0
[9 empty] | 4 | 0 | 0 | 0 | 0
[9 empty] | 5 | 0 | 0 | 0 | 0 | 0
[9 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 12 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1

## Ref Battery (hidden)
Battery Size (kWh) | TSB-10 | 3.8 |  |  | 7.6 |  |  | 11.4
|  | Charge | Discharge - Cont | Discharge - Surge | Charge | Discharge - Cont | Discharge - Surge | Charge | Discharge - Cont | Discharge - Surge
0 | 1
9900 | 1 | 3800 | 3800 | 3800 | 5200 | 5200 | 5200 | 5200 | 5200 | 5200
19800 | 2 | 3800 | 3800 | 3800 | 7600 | 7600 | 7600 | 10400 | 10400 | 10400
39600 | 4 | 3800 | 3800 | 3800 | 7600 | 7600 | 7600 | 10400 | 10400 | 10400
1 Port Used (1 Battery Cabinet)
Load Power | Surge Power | 3.8 | 7.6 | 11.4 |  | MPPTs
0 | 0 | 1 | 0 | 0 |  | 2
3800 | 3800 | 1 | 0 | 0 |  | 2
5200 | 5200 | 0 | 1 | 0 |  | 3
5200 | 5200 | 0 | 0 | 1 |  | 4
2 Ports Used (>2 Battery Cabinets)
Load Power | Surge Power | 3.8 | 7.6 | 11.4 |  | MPPTs
0 | 0 | 1 | 0 | 0 |  | 2
3800 | 3800 | 1 | 0 | 0 |  | 2
7600 | 7600 | 0 | 1 | 0 |  | 3
10400 | 10400 | 0 | 0 | 1 |  | 4
4 Battery Cabinets
0 | 0 | 1 | 0 | 0 |  | 2
3800 | 3800 | 1 | 0 | 0 |  | 2
7600 | 7600 | 0 | 1 | 0 |  | 3
10400 | 10400 | 0 | 0 | 1 |  | 4
18000 | 18000 | 0 | 1 | 1 |  | 7
20800 | 20800 | 0 | 0 | 2 |  | 8

## Ref Bat & Sol (hidden)
Grid Voltage | Inverter Efficiency | Degrees | Inverter Standy Power |  |  | Type
240 | 97.5% | C | 50 | W |  | Rooftop
208 |  | F |  |  |  | Ground Mount
|  |  | Qty |  |  |  |  | Module Quantities / MPPT
| Modules | MPPTs Req. | 3.8 | 7.6 | 11.4 | ID | MPPTs | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| 8 | 1 | 1 | 0 | 0 | 1 | 1 | 52
| 16 | 2 | 1 | 0 | 0 | 2 | 2 | 26 | 26
| 20 | 2 | 0 | 1 | 0 | 3 | 3 | 17 | 17 | 18
| 30 | 3 | 0 | 1 | 0 | 4 | 4 | 13 | 13 | 13 | 13
| 40 | 4 | 0 | 0 | 1 | 5 | 5 | 10 | 10 | 10 | 11 | 11
| 60 | 6 | 0 | 2 | 0 | 7 | 6 | 8 | 8 | 9 | 9 | 9 | 9
| 80 | 8 | 0 | 0 | 2 | 9 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 8
[7 empty] | 8 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7

## Loads (hidden)
Name | Operating Power | Surge Power | Daily Usage
| Watts | Watts | Hrs
None | 0 | 0 | 0
Air Conditioner | 3500 | 18720 | 2
Coffee Machine | 800 | 800 | 1
Dishwasher | 1400 | 1400 | 1.1
Electric Clothes Dryer | 3000 | 4500 | 1
Electric Oven/Stove | 2100 | 2100 | 0.5
Electric Vehicle | 7700 | 7700 | 4
Electric Water Heater
Electric Heater - Portable | 1200 | 1200 | 4
Freezer | 300 | 300 | 24
Garage Door Opener | 650 | 1200 | 0.05
Gas Furnace - 1/2 HP | 800 | 2350 | 4
Hair Dryer | 1500 | 1500 | 0.1
Laptop / PC | 100 | 100 | 6.3
Lights | 20 | 20 | 10.5
Microwave | 1200 | 1200 | 0.6
Mobile Charger | 10 | 10 | 2.1
Refrigerator | 400 | 800 | 9
Sump Pump - 1/3 HP | 800 | 1300 | 2
Tankless Electric Water Heater
Television | 80 | 80 | 3.5
Vacuum Cleaner | 1000 | 1000 | 0.5
Washing Machine | 500 | 500 | 2.2
Gas Water Heater
Well Pump | 1920 | 4560 | 0.5
Wifi Router | 10 | 10 | 10
Minisplit Heat/AC | 2500 | 6000
Heat Pump | 4700 | 10000