## Cover
PUNCH LIST
A defects register for Australian construction projects, run from the client side. It carries Pre-Practical Completion items and Defects Liability Period defects in one list, tracks who each item sits with, and ages every item from the day it was raised - including the ones that fail re-inspection.
HOW TO USE IT
1 | Set up the project once | Fill in the Setup sheet: project, contract, parties, the Date for Practical Completion and the Defects Liability Period. The register and the sign-off sheet both read from it.
2 | Set your areas and trades | The Area and Trade columns are dropdowns driven by the Reference sheet. Edit those lists to match your project before the first inspection - it is what makes the Summary sheet useful.
3 | Raise items during the inspection | One row per item. Write what is wrong AND what will fix it in the same cell - an item that only says 'paint poor' will be argued about.
4 | Set severity and PC impact | These two columns are the ones the Superintendent will be asked about. Only mark an item as stopping PC if you would genuinely withhold the certificate for it.
5 | Set a target date and an owner | The Contractor allocates the subcontractor; the Superintendent sets the target. Items with no target date show as 'no target' and never appear as overdue - they just quietly rot.
6 | Only the Superintendent closes | The Contractor moves items to Ready for inspection. The Superintendent then sets Closed or Not accepted. Not accepted keeps the item ageing from the original raised date, which is the point.
7 | Work from the Summary sheet | It shows who owes what, by trade and by area, with ageing buckets and the count of open items that stop Practical Completion. That is the list you take to the site meeting.
THE COLOUR CODE
| Status |  | Severity and impact
| Open |  | Critical | Life safety, compliance, or the asset cannot be used.
| In progress |  | Major | Function, durability or appearance materially affected.
| Ready for inspection |  | Minor | Cosmetic or minor finish item.
| Not accepted |  | Stops PC | Must be closed before Practical Completion is certified.
| Closed |  | OVERDUE | Past its target date and still open.
Not a defect
On hold
WHAT IS IN THE WORKBOOK
| Sheet | Purpose
| Setup | Project, contract, parties, key dates and the basis on which an item is accepted as closed.
| Punch List | The register. Pre-Practical Completion and Defects Liability Period items in one list, colour-coded by status and severity.
| Summary | Live counts by status, severity, stage, trade and area, with ageing buckets.
| Inspection Sign-off | Printable record of an inspection: attendees, the register position, the outcome and signatures.
| Photo Log | Before and after photo references against each item ID.
| Reference | Dropdown lists, status and severity definitions, and the cell conventions.
IMPORTANT
This register is a working tool, not legal advice. What amounts to a defect, who bears the cost of rectification, and whether an item prevents Practical Completion are all governed by the contract. Record the basis of acceptance on the Setup sheet before the first inspection, and check the contract before withholding Practical Completion over any item.
Built for capital project teams by Mastt. Project controls, cost management and reporting · mastt.com

## Setup
PROJECT SETUP
Complete once. The register, the summary and the sign-off sheet all read from here.
Blue cells are yours. Off-white cells calculate themselves.
1 · PROJECT & CONTRACT
Project name
Project number
Site address
Contract title
Contract number
Contract form
2 · PARTIES
Principal / Client
Contractor
Contractor site contact
Superintendent / Certifier
Certifier organisation
Register owner
3 · KEY DATES
Date for Practical Completion (adjusted)
Actual Date of Practical Completion |  | Leave blank until PC is certified.
Defects Liability Period (months)
End of the Defects Liability Period
Standard rectification period (days) |  | Used as the default gap between the date raised and the target date.
Register revision
Date this revision was issued
4 · BASIS OF ACCEPTANCE
An item is closed when it complies with | the Contract, the approved drawings and specification, the National Construction Code and the relevant Australian Standards.
Write the basis of acceptance down before the first inspection. Most punch list arguments are not about whether something is imperfect - they are about what standard applies.
Built with Mastt ¦ mastt.com

## Punch List
PUNCH LIST · DEFECTS REGISTER
Open 9 Overdue 2 Stops PC 5 Closed 1
EXAMPLE DATA · delete rows 9 to 18 and the Photo Log examples before use
Item ID | Stage | Raised | Area / building | Level | Room / grid ref | Trade / package | Category | Description of the item and the rectification required | Severity | Stops PC? | Responsible | Subcontractor allocated | Target | Status | Rectified | Closed | Closed out by | Days open | Flag | Photos | Comments
PL-001 | Pre-Practical Completion | 2026-07-27 | Building A | L3 | Rm 3.04 | Painting | Defect | Paint finish to the south wall shows roller marks and visible patching under natural light. Repaint the full wall to a uniform finish. | Minor | No | Contractor | Coastal Painting Pty Ltd | 2026-08-21 | In progress |  |  |  | 15 | in 10d | 0 | EXAMPLE - delete before use
PL-002 | Pre-Practical Completion | 2026-07-27 | Building A | L1 | Main lobby | Facade and glazing | Damage | Chip to the lower right corner of glazing panel G-12. Replace the panel and reinstate the seal. | Major | Yes | Contractor | Vitrex Facades Pty Ltd | 2026-08-18 | Open |  |  |  | 15 | in 7d | 1 | EXAMPLE
PL-003 | Pre-Practical Completion | 2026-07-28 | Roof and plant | Roof | Plant deck | Mechanical services | Incomplete work | Condensate drain to AHU-03 is not connected to the waste. Complete the connection and witness test. | Critical | Yes | Contractor | Apex Mechanical Services | 2026-08-12 | Ready for inspection | 2026-08-07 |  |  | 14 | in 1d | 0 | EXAMPLE
PL-004 | Pre-Practical Completion | 2026-07-22 | Basement | B1 | Carpark egress | Electrical services | Non-conformance | Emergency lighting to the carpark egress path does not achieve the required illuminance. Rectify to comply with AS 2293.1 and provide a compliance certificate. | Critical | Yes | Contractor | Arcline Electrical Pty Ltd | 2026-08-05 | Not accepted | 2026-08-03 |  |  | 20 | OVERDUE 6d | 2 | EXAMPLE
PL-005 | Pre-Practical Completion | 2026-07-24 | External and landscape | GF | Forecourt | Landscaping and external works | Incomplete work | Paving to the forecourt is not laid to the eastern edge. Complete in accordance with drawing L-102. | Major | No | Contractor | Greenline Landscapes | 2026-08-07 | Open |  |  |  | 18 | OVERDUE 4d | 0 | EXAMPLE
PL-006 | Pre-Practical Completion | 2026-07-20 | Building A | L2 | Rm 2.11 | Ceilings | Defect | Ceiling tile grid is out of level by 8 mm over 3 m. Adjust to the specified tolerance. | Minor | No | Contractor | Interior Linings Co | 2026-08-10 | Closed | 2026-08-04 | 2026-08-06 | A. Whitmore | 17 |  | 1 | EXAMPLE
PL-007 | Pre-Practical Completion | 2026-07-30 | Building A | L1 | Comms room | Security and communications | Missing documentation | As-built drawings and the O&M manual for the access control system have not been provided. | Major | Yes | Contractor | Sentry Systems Pty Ltd | 2026-08-24 | Open |  |  |  | 12 | in 13d | 0 | EXAMPLE
PL-008 | Pre-Practical Completion | 2026-08-03 | Site wide | All | Levels 2-3 | Cleaning | Cleaning | Builder's clean not completed to levels 2 and 3. Complete prior to the Practical Completion inspection. | Minor | Yes | Contractor | Sparkle Site Services | 2026-08-14 | Open |  |  |  | 8 | in 3d | 0 | EXAMPLE
PL-009 | Defects Liability Period | 2026-08-04 | Building A | L1 | Accessible WC | Hydraulic services | Defect | Intermittent leak at the basin mixer in the ground floor accessible WC. Investigate and rectify. | Major | No | Contractor | Metro Plumbing Group | 2026-08-26 | Open |  |  |  | 7 | in 15d | 0 | EXAMPLE
PL-010 | Defects Liability Period | 2026-08-05 | Building A | L3 | Rm 3.08 | Floor finishes | Defect | Vinyl seam lifting at the doorway threshold. Re-weld the seam and make good. | Minor | No | Contractor | Surface Floors Pty Ltd | 2026-09-02 | In progress |  |  |  | 6 | in 22d | 0 | EXAMPLE
One item per row. Write what is wrong AND what will fix it in the description - an item that only says 'poor finish' will be argued about. Only the Superintendent sets Closed; the Contractor moves items to Ready for inspection. 'Not accepted' keeps the item ageing from the date it was first raised, which is the point of it. Add rows inside the table so the Summary keeps counting them. Prints A3 landscape - for A4, hide columns F, G, S and W first. The four grey columns - Item ID, Days open, Flag and Photos - calculate themselves; everything else is yours to fill in.
Built with Mastt ¦ mastt.com
Formulas:
Days open = IF(J9="","",IF([Closed]<>"",[Closed]-[Raised],IF([Raised]="","",TODAY()-[Raised])))
Flag = IF(J9="","",IF(OR([Status]="Closed",[Status]="Not a defect"),"",IF([Target]="","no target",IF([Target]<TODAY(),"OVERDUE "&(TODAY()-[Target])&"d","in "&([Target]-TODAY())&"d"))))

## Summary
SUMMARY
Who owes what, where, and how long it has been sitting there
EXAMPLE DATA is still in the register
WHERE THE LIST STANDS
Total items raised |  | 10 |  | Items overdue |  | 2
Open items |  | 9 |  | Open items that stop PC |  | 5
Closed items |  | 1 |  | Open Critical items |  | 2
Percentage closed |  | 10% |  | Open more than 30 days |  | 0
Trade and area counts show OPEN items only - that is the chase list.
BY STATUS |  |  |  | BY TRADE
Status | Items | % of all | Share | Trade | Items | % of all | Share
Open | 5 | 50% | ¦¦¦¦¦¦¦¦¦¦¦¦¦ | Demolition | 0 | 0%
In progress | 2 | 20% | ¦¦¦¦¦ | Earthworks and civil | 0 | 0%
Ready for inspection | 1 | 10% | ¦¦¦ | Piling and foundations | 0 | 0%
Not accepted | 1 | 10% | ¦¦¦ | Concrete structure | 0 | 0%
Closed | 1 | 10% | ¦¦¦ | Structural steel | 0 | 0%
Not a defect | 0 | 0% |  | Masonry | 0 | 0%
On hold | 0 | 0% |  | Carpentry and joinery | 0 | 0%
|  |  |  | Roofing and cladding | 0 | 0%
BY SEVERITY |  |  |  | Facade and glazing | 1 | 10% | ¦¦¦
Severity | Items | % of all | Share | Windows and doors | 0 | 0%
Critical | 2 | 20% | ¦¦¦¦¦ | Waterproofing | 0 | 0%
Major | 4 | 40% | ¦¦¦¦¦¦¦¦¦¦ | Plastering and linings | 0 | 0%
Minor | 4 | 40% | ¦¦¦¦¦¦¦¦¦¦ | Partitions | 0 | 0%
|  |  |  | Ceilings | 0 | 0%
BY STAGE |  |  |  | Painting | 1 | 10% | ¦¦¦
Stage | Items | % of all | Share | Floor finishes | 1 | 10% | ¦¦¦
Pre-Practical Completion | 8 | 80% | ¦¦¦¦¦¦¦¦¦¦¦¦¦¦¦¦¦¦¦¦¦ | Tiling | 0 | 0%
Defects Liability Period | 2 | 20% | ¦¦¦¦¦ | Hydraulic services | 1 | 10% | ¦¦¦
|  |  |  | Mechanical services | 1 | 10% | ¦¦¦
AGEING OF OPEN ITEMS |  |  |  | Electrical services | 1 | 10% | ¦¦¦
Age | Items | % of open | Share | Fire services | 0 | 0%
0 - 7 days | 2 | 22.22% | ¦¦¦¦¦¦ | Vertical transport | 0 | 0%
8 - 14 days | 3 | 33.33% | ¦¦¦¦¦¦¦¦¦ | Security and communications | 1 | 10% | ¦¦¦
15 - 30 days | 4 | 44.44% | ¦¦¦¦¦¦¦¦¦¦¦¦ | Landscaping and external works | 1 | 10% | ¦¦¦
31 - 60 days | 0 | 0% |  | Signage and wayfinding | 0 | 0%
Over 60 days | 0 | 0% |  | Loose furniture and equipment | 0 | 0%
|  |  |  | Cleaning | 1 | 10% | ¦¦¦
|  |  |  | Other | 0 | 0%
BY AREA
|  |  |  | Area | Items | % of all | Share
|  |  |  | Building A | 5 | 50% | ¦¦¦¦¦¦¦¦¦¦¦¦¦
|  |  |  | Building B | 0 | 0%
|  |  |  | Basement | 1 | 10% | ¦¦¦
|  |  |  | Ground floor | 0 | 0%
|  |  |  | Podium | 0 | 0%
|  |  |  | Tower | 0 | 0%
|  |  |  | Roof and plant | 1 | 10% | ¦¦¦
|  |  |  | Carpark | 0 | 0%
|  |  |  | External and landscape | 1 | 10% | ¦¦¦
|  |  |  | Site wide | 1 | 10% | ¦¦¦
Every figure here is a formula over the Punch List sheet. 'Open' means anything not Closed and not marked Not a defect. Ageing runs from the date the item was raised, not from the last time it was re-inspected, so items that keep failing keep ageing.
Built with Mastt ¦ mastt.com

## Inspection Sign-off
INSPECTION SIGN-OFF
INSPECTION DETAILS
Inspection type
Date of inspection
Time started
Time finished
Areas inspected
Weather and site conditions
Inspection reference
ATTENDEES
Name | Organisation | Role | Signature
THE REGISTER AT THE DATE OF THIS INSPECTION
Total items on the register | 10
Open items | 9
Open items that stop Practical Completion | 5
Open Critical items | 2
Items overdue | 2
OUTCOME
Outcome of this inspection
The Superintendent has inspected the areas listed above and records the items on the Punch List sheet as the items requiring rectification. Items marked as stopping Practical Completion must be closed out and verified before Practical Completion can be certified. This sign-off records the inspection only; it is not a certificate of Practical Completion, an approval of the work, or an acceptance that the work is free from defects that were not apparent at the time of inspection.
Superintendent / Certifier
Name |  | Position
Signature |  | Date
Contractor representative
Name |  | Position
Signature |  | Date
Built with Mastt ¦ mastt.com

## Photo Log
PHOTO LOG
One row per photo. Enter the Item ID exactly as it appears in column B of the Punch List (PL-001, PL-002 and so on) - the register counts the photos back against each item.
Item ID | Photo reference | Type | Date taken | Taken by | File name or location | What the photo shows
PL-002 | IMG-2207-01 | Before | 2026-07-27 | A. Whitmore | Site photos / 2026-07-27 PC inspection / IMG-2207-01.jpg | Chip to glazing panel G-12, lower right corner.
PL-004 | IMG-2207-14 | Before | 2026-07-22 | A. Whitmore | Site photos / 2026-07-22 services walk / IMG-2207-14.jpg | Lux meter reading at the carpark egress path.
PL-004 | IMG-2208-03 | After | 2026-08-03 | S. Nguyen | Site photos / 2026-08-03 rectification / IMG-2208-03.jpg | Reading after the first rectification attempt - still below the required level.
PL-006 | IMG-2208-09 | After | 2026-08-04 | S. Nguyen | Site photos / 2026-08-04 rectification / IMG-2208-09.jpg | Ceiling grid re-levelled and checked.
Record the file location as text - keep the photos in your document management system rather than embedding them here, or the workbook will become too heavy to email. A Before and an After photo against every Major and Critical item makes close-out arguments very short.
Built with Mastt ¦ mastt.com

## Reference
REFERENCE · DROPDOWN LISTS & CONVENTIONS
Edit the Area and Trade lists to match your project before the first inspection. Add values inside the ranges, not below them, so the dropdowns pick them up.
Stage | Trade / package | Category | Severity | Status | Responsible party | Area / building | Yes / No | Photo type | Inspection type
Pre-Practical Completion | Demolition | Defect | Critical | Open | Contractor | Building A | Yes | Before | Pre-Practical Completion inspection
Defects Liability Period | Earthworks and civil | Incomplete work | Major | In progress | Principal | Building B | No | After | Practical Completion inspection
| Piling and foundations | Non-conformance | Minor | Ready for inspection | Principal's separate contractor | Basement |  | Context | Re-inspection
| Concrete structure | Damage |  | Not accepted | Consultant | Ground floor |  | Close-up | Defects Liability Period inspection
| Structural steel | Missing documentation |  | Closed | Supplier | Podium |  |  | Final inspection - end of DLP
| Masonry | Cleaning |  | Not a defect | Under investigation | Tower
| Carpentry and joinery | Commissioning outstanding |  | On hold |  | Roof and plant
| Roofing and cladding |  |  |  |  | Carpark
| Facade and glazing |  |  |  |  | External and landscape
| Windows and doors |  |  |  |  | Site wide
Waterproofing
Plastering and linings
Partitions
Ceilings
Painting
Floor finishes
Tiling
Hydraulic services
Mechanical services
Electrical services
Fire services
Vertical transport
Security and communications
Landscaping and external works
Signage and wayfinding
Loose furniture and equipment
Cleaning
Other
STATUS DEFINITIONS
Open | Raised and issued to the Contractor. Nothing has started.
In progress | The Contractor has started rectification.
Ready for inspection | The Contractor says it is done. Waiting on the Superintendent to verify.
Not accepted | Re-inspected and failed. Back to the Contractor - the item stays open and keeps ageing.
Closed | Verified by the Superintendent and signed off. Only the Superintendent sets this.
Not a defect | Assessed and found to be within tolerance, out of scope, or the Principal's responsibility. Record the reasoning in the comments.
On hold | Cannot proceed - awaiting a decision, access, a long-lead part or another trade.
SEVERITY
Critical | Life safety, statutory compliance, or the asset cannot be used or operated. Always stops Practical Completion.
Major | Function, durability or appearance is materially affected. Usually stops Practical Completion in the affected area.
Minor | Cosmetic or minor finish item. Normally rectified during the Defects Liability Period rather than holding up Practical Completion.
CELL CONVENTIONS
You complete this | Pale blue fill, blue text.
Calculated | Off-white fill. A formula - do not type over it.
Subtotal or total | Light grey with a rule above. Always a formula.
Section band | Marks the start of a section.
Built with Mastt ¦ mastt.com