
	[image: image1.jpg]AlUMAam

architectural fire-rated solutions




	Aluflam North America

16604 Edwards Road
Cerritos, CA 90703
Phone: 562.926.9520
Website: www.aluflam-usa.com


Aluflam Fire-Rated Aluminum Full Vision Doors and Frames – 
3-Part Specification

	Notes to Specifier:
This product specification is written to assist specifiers in the preparation of project specifications.  The section must be carefully reviewed and edited to meet the requirements of the project and local building code.

Section numbers are from MasterFormat 1995 Edition, with numbers from MasterFormat 2004 Edition in parentheses. Delete the version that is not required.

Notes to the specifier are contained in boxes and should be deleted from final copy.  Optional items requiring selection by the specifier are enclosed within brackets and highlighted in yellow.  Make appropriate selections and delete others.

When editing is complete, delete all text on this page, then remove the section break at the top of the next page to remove this page from the document.

For assistance, call Aluflam North America at 562.926.9520.




SPECIFICATION BEGINS ON THE FOLLOWING PAGE.

SECTION 08120 (08 11 16)

FIRE-RATED ALUMINUM FULL VISION DOORS AND FRAMES

PART 1 - GENERAL

1.01 SECTION INCLUDES
A. 
Fire-rated aluminum full vision Aluflam door system including pre-finished door, frame, glazing, and hardware.

1.02 RELATED SECTIONS
A. Section 08710 (08 71 00): Door Hardware.
B. Section 08817 (08 88 17): Fire-Rated Glass & Framing.

1.03 REFERENCES

A.
American Society for Testing and Materials (ASTM):

1. ASTM E119 Standard Test Methods for Fire Tests of Building Construction and Materials.

2. ASTM E2074 Standard Test Method for Fire Tests of Door Assemblies, Including Positive Pressure Testing of Side-Hinged and Pivoted Swinging Door Assemblies.

B.
National Fire Protection Association (NFPA):

1. NFPA 80: Standard for Fire Doors and Fire Windows.

2. NFPA 251: Standard Methods of Tests of Fire Endurance of Building Construction and Materials.

3. NFPA 252: Standard Methods of Fire Tests of Door Assemblies.

C.
Uniform Building Code (UBC):

1. UBC-7-2: Methods for Fire Tests of Door Assemblies.

D.
Underwriters Laboratories, Inc. (UL):

1. UL 10C: Positive Pressure Fire Tests of Door Assemblies.

E.
Standard Council of Canada:

1. ULC Standard CAN4-S104: Fire Tests of Door Assemblies. 

F.
American National Standards Institute (ANSI):

1. ANSI Z97.1 Safety Glazing Materials Used in Buildings – Safety Performance Specifications and Methods of Test. 

G.
Consumer Product Safety Commission (CPSC):

1. CPSC 16 CFR 1201 Categories I and II:  Safety Standard for Glazing Materials. 

1.04 SYSTEM DESCRIPTION
A.
Performance Requirements: 

	Notes to Specifier:  Select fire rating to meet building code requirements.


1. Fire Rating: [20] [45] [60] [90] minutes.

2. Certification: Doors and frames shall be tested in accordance with ASTM E 2074, NFPA 252, UBC 7-2, UL 10C, CAN4-S104.
3. Testing Laboratory: Fire tests shall be conducted by an approved independent testing laboratory, similar to Underwriter’s Laboratories, Inc.

1.05 SUBMITTALS

A.
Submit listed submittals in accordance with Conditions of the Contract and Division 1 Submittal Procedure Section.

1. Shop Drawings: Submit shop drawings showing layouts, profiles and product components. 

2. Samples: Submit samples for finishes, colors and textures.

3. Technical Information: Submit latest edition of manufacturer’s product data providing product description, technical data and installation instructions.

1.06 QUALITY ASSURANCE
A.
Listings and Labels:
Fire rated framing and glazing shall be under current follow-up services by an approved independent agency and maintain a current listing or certification. Assemblies shall be labeled in accordance with limits of listings. 
1.07 DELIVERY, STORAGE AND HANDLING

A.
Ordering: Comply with manufacturer’s ordering instructions and lead-time requirements to avoid construction delays.
B.
Delivery: Deliver materials to specified destination in manufacturer’s packaging undamaged, complete with installation instructions. 
C.
Storage and Protection: Store off ground, under cover, protected from weather, direct sunlight, construction activities and at temperature conditions recommended by manufacturer, +10°F to +110°F.

D.  Handling: Protect materials and finish during handling and installation to prevent damage.
1.08 PROJECT CONDITIONS

A.
Field Measurements: Verify actual measurements for openings by field measurements before fabrication. Show recorded measurements on shop drawings. Coordinate field measurements and fabrication schedule with construction progress to avoid construction delays.

PART 2 - PRODUCTS

2.01 FIRE-RATED ALUMINUM FULL VISION DOORS AND FRAMES 
A.
Manufacturer: Aluflam North America
1. Contact: 16604 Edwards Road, Cerritos, CA 90703: Telephone 562.926.9520 Fax 562.404.1394.  E-mail info@aluflam-usa.com Website  www.aluflam-usa.com, or local representative (www.aluflam-usa.com/contact/representatives.php).
2.02 MATERIALS – ALUMINUM FRAMING
A. Frame construction:  Integral structure and glazing stops from extruded and thermally broken aluminum profiles.  Filled internally with cement composite material.

B. Dimensions:
1.  Door framing face dimension:  2-½ inch
2.  Depth of door framing:  3-7/16 inch (3-5/8 for 90 Min Door)
3.  Door stile face dimension:  3-9/16 inch (3-3/4 for (90 Min Door) 
4.  Door cross rail (if applicable):  3-9/16 inch (N/A for 90 Min Door)
C. Assembly:  Frame corners assembled by means of crimped and bonded miter joints.


D. Sealing:  Framing system shall insulate against effects of fire, smoke, and heat transfer from either side. Perimeter of the framing system to the rough opening shall be firmly packed with mineral wool insulation.

2.03 MATERIALS – FIRE RESISTANT GLAZING
	Notes to Specifier:  Select glazing type based on fire rating of system.


A. Assemblies shall be glazed with [20 minute rated 3/16 inch thick SGG Pyroswiss], [45 minute rated ¾ inch thick SGG Contraflam 45], [60 minute rated 1 inch thick SGG Contraflam 60], [90 minute rated 1-3/8 inch thick SGG Contraflam 90]  fire resistant glazing material as manufactured by Vetrotech Saint-Gobain (www.vetrotechusa.com). 

1. Individual lites shall be permanently identified with a listing mark.

2. Glazing material installed in “Hazardous Locations” (subject to human impact) shall be certified to meet the applicable requirements for fire rated assemblies referenced in ANSI Z97.1 Standard for Safety Glazing Materials Used In Buildings and/or CPSC 16 CFR 1201 Safety Standard for Architectural Glazing Materials.

3. Visible daylight transmission shall be a minimum of 81%. Glazing material shall be optically clear, colorless and free from unusual distortion.
	Notes to Specifier:  Specify the following paragraph for exterior applications.


B. Fire-rated glazing shall be insulated with ¼” airgap (½” airgap for 20 or 45 min glazing)  and ¼” low-E coated outboard glass lite.  Installation conditions shall be analyzed to assure that fire-rated glazing is not exposed to temperatures outside the 10 – 110 degrees F limits.
2.04 MATERIALS – GLAZING AND ASSEMBLY ACCESSORIES
A. Fasteners: All fasteners, setting pads, and glazing clips, shall be stainless or zinc-plated steel.


B.
Glazing Accessories: The glazing material perimeter shall be separated from the perimeter framing system with approved flame retardant intumescent glazing tape.  Ceramic setting blocks shall be placed between the metal setting pads and the glazing material. Setting pads and blocks provided by manufacturer. 
2.05 FABRICATION

A. Door frames and door leaves shall be furnished pre-assembled. Door assemblies shall be field glazed.

B. Door assemblies shall be factory prepared for field mounting of hardware.

C. Fabrication Dimensions:  Fabricate to approved dimensions.  The general contractor shall guarantee dimensions within required tolerance (+ - 1/8”).  Obtain approved shop drawings prior to fabrication.
 
2.06 FINISHES

A.
Framing shall be chemically cleaned and pretreated, then finished on all exposed areas with: 
	Notes to Specifier:  Select finish and color.


[Anodized – Clear] [Anodized – Light Bronze] [Anodized – Medium Bronze] [Anodized – Dark Bronze] [Powder Coated Epoxy – Color RAL#XXXX] [Fluropolymer Paint – Kynar/Duranar UC Code XXXXX]. 

B.
Protect finishes on exposed surfaces from damage by applying a strippable, temporary protective covering before shipping.


C.  Slight variations in appearance of abutting or adjacent pieces are acceptable.  Noticeable variations in the same piece are not acceptable. 
2.07 DOOR HARDWARE

A. Hardware shall be supplied from door manufacturer’s standard recommended hardware groups as specified.


	Notes to Specifier:  Select hardware schedule(s) based on door configuration.  Consult with Aluflam prior to specifying alternative hardware or hardware finishes.  Hardware denoted with *) is optional.


[B.  Operating hardware for single doors. Each to have the following:

	Quantity
	Description
	Manufacturer/Model
	Finish

	1
	Surface applied door closer
	Dorma TS93 series
	Aluminum

	3 
	Surface applied hinges (Qty 4 on 90 min door) 
	Dr Hahn A901/951 series
	Aluminum

	2
	Lever handles
	FSB 1080 series
	Stainless

	1
	Narrow stile mortise lock
	Accurate 8600 series
	Stainless (front)

	1
	Cylinder lock
	Schlage compatible
	Satin chrome

	1
	*) Rim based exit device – (Standard on 90 min door)
	Dorma 9700
	Stainless

	1
	*) 10” bottom kickplate
	Aluflam
	Match door finish

	1
	*) Automatic floor seal
	Planet MF
	Aluminum

	
	
	
	


Balance of hardware by others]
 
[C.  Operating hardware for active/inactive pairs of doors (Not available in 90 Min rating. Each to have the following:

	Quantity
	Description
	Manufacturer/Model
	Finish

	1
	Surface applied door closer/coordinator
	Dorma TS93-1GSR series
	Aluminum

	6
	Surface applied hinges 
	Dr Hahn A901 series
	Aluminum

	2
	Lever handles
	FSB 1080 series
	Stainless

	1
	Narrow stile mortise lock
	Accurate 8600 series
	Stainless (front)

	1
	Automatic flush bolt 
	BKS B1899/1895
	Stainless

	1
	Cylinder lock
	Schlage compatible
	Satin chrome

	1
	Thumbturn
	FSB 1709 series
	Stainless

	1
	*) Rim based exit device 
	Dorma 9700
	Stainless

	2
	*) 10” bottom kickplate
	Aluflam
	Match door finish

	2
	*) Automatic floor seal
	Planet MF
	Aluminum


Balance of hardware by others]
[D.  Operating hardware for active/active pairs of doors. Each to have the following:

	Quantity
	Description
	Manufacturer/Model
	Finish

	2
	Surface applied door closers
	Dorma TS93 series
	Aluminum

	6
	Surface applied hinges (Qty 8 for 90 Min Doors)
	Dr Hahn A901/951 series
	Aluminum

	2
	Vertical rod exit devices (top rod only for 60 min and lower rated, 90 min - top & bottom rods) 
	Dorma 9800 series
	Stainless

	2
	*) 10” bottom kickplate
	Aluflam
	Match door finish

	2
	*) Automatic floor seal
	Planet MF
	Aluminum


Balance of hardware by others]
 

PART 3 - EXECUTION

3.01 EXAMINATION

A.
Examine area to receive doors.  Openings shall be plumb, square and within allowable tolerances.  Notify Architect of conditions that would adversely affect installation or subsequent use.  Do not proceed with installation until unsatisfactory conditions are corrected. 

3.02 INSTALLATION

A.
Door installation shall be by a specialty contractor with appropriate experience qualifications; and in strict accordance with the approved shop drawings.

3.03 CLEANING

A.
Cleaning: Remove temporary coverings and protection of adjacent work areas. Glass and frame should be cleaned using soft clean cloth, chamois leathers, sponges or soft paper.  Use clean warm water with a mild detergent. Do not use detergent that contains either alkaline, acids or fluoride! Abrasive cleaning methods can damage surfaces!  Clean prior to owner’s acceptance. Remove construction debris from project site and legally dispose of debris. 

END OF SECTION

PAGE  
Project Name/Number/Date
08120 (08 11 16) - 5
Fire-Rated Aluminum Doors and Frames

