SUBMITTAL DATA SHEET

AUX R32 - The Free Match Inverter Series - ASUM18HPMULO

| Job Name | Location Date |
| --- | --- |
| Purchaser | Engineer |
| Submitted to | For □Reference □Approval □Construction |
| Unit Designation | Schedule # |

ASUM18HPMULO

- AHRI No: 214291428

- One Person Installation

- 3 Ways to Control (Voice, Wi-Fi & Remote)

- Highly Performance

- Outdoor Unit PCB Coating

- Easy Service Control Board

- Golden Fin

- Wide Voltage Operation

Submittal Data Sheet - ASUM18HPMULO

| Specifications |  |  |  |  |
| --- | --- | --- | --- | --- |
| DC INVERTER | Model |  |  | ASUM18HPMULO |
| System Format |  |  |  | 1 drive 2 |
| Capacity | Cooling |  | Btu/h | 18000(4800-25000) |
|  | Heating |  | Btu/h | 21000(5000-26000) |
| Cooling | Capacity | Rated | Btu/h | 18000 |
|  | Capacity Range | Min-Max | Btu/h | 4800-25000 |
|  | Power Input | Rated | W | 1440 |
|  | Moisture Removal |  | Kg/h | 3 |
| Heating | Capacity at 47℉ | Rated | Btu/h | 21000 |
|  | Capacity Range | Min-Max | Btu/h | 5000-26000 |
|  | Power Input at 47℉ | Rated | W | 1620 |
|  | Capacity at 17℉ | Rated | Btu/h | 18100 |
|  | Capacity at 5℉ | Max | Btu/h | 21800 |
|  | Capacity at -5℉ | Max | Btu/h | 14700 |
| Electric Data | Power Supply |  | V~,Hz,Ph | 208~230,60,1 |
|  | Cooling Power Input |  | W | 1440 |
|  | Heating Power Input |  | W | 1620 |
|  | Rated Current (cooling & heating) |  | A | 6.40/7.18 |
|  | Max current |  | A | 18 |
|  | MCA |  | A | 20 |
|  | MOCP |  | A | 30 |
|  | Max power |  | KW | 3.8 |
| Efficiency | SEER |  | W/W | 23.3 |
|  | HSPF |  | W/W | 11 |
|  | EER/COP |  | W/W | 3.66/3.80 |
| Air Flow Volume |  |  | CFM | 2235 |
| Noise Level | Sound Pressure Noise Level |  | dB(A) | 58 |
|  | Sound Power Noise Level |  | dB(A) | 68 |
| Dimension | Net Dimension (W*D*H) |  | inch | 38.58×15.28×27.56 |

|  | Packing Dimension (W*D*H) | inch | 39.96×16.73×30.00 |
| --- | --- | --- | --- |
| Weight | Net/Gross | lbs | 104.7/111.3 |
| Refrigerant | Type | - | R32 |
|  | Charged Volume | Oz/kg | 49.4/1.4 |
|  | Additional charge | (oz/ft)/(g/m) | 0.16/15 |
| Piping | Liquid Side | inch(mm) | 1/4(6.35)x2 |
|  | Gas Side | inch(mm) | 3/8(9.52)x2 |
|  | Max. length for all rooms (m) | Ft/m | 131/40 |
|  | Max. length for one IDU (m) | Ft/m | 82/25 |
|  | Max. height difference between IDU and OU (m) | Ft/m | 49/15 |
|  | Max. height difference between IDUs (m) | Ft/m | 33/10 |
|  | Adapter | - | NO |
| Ambient Temp (Cooling/Heating) |  | ℉ | -13~125℉/-22~75℉ |

Remarks:

1.All specifications are subject to change by the manufacturer without prior notice.

2.All units are being tested and comply to ISO5151.

3.Sound pressure levels are measured in anechoic chamber.

During actual operation, sound pressure level will be higher as a result of room specification condition.

4.Data from AUX lab,05/03/24, Data may change according to test surroundings, AUX reserves right of explanation on data.

Submittal Data Sheet - ASUM18HPMULO

Submittal Data Sheet - ASUM18HPMULO

| Model # | Capacity (Btu/H) | Max Combination Ratio | Number of Ports |
| --- | --- | --- | --- |
| ASUM18HPMULO | 18K | 133% | 2 |

| Suggested Combination | 1 Drive 2 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Two Units | 9+9 | 9+12 | 12+12 |  |  |  |

| Applicable IDU models |  |  |  |
| --- | --- | --- | --- |
| 09K AFEB09HP230V1CH | 12K AFEB12HP230V1CH |  |  |

Note：

1. All above indoor units can be freely matched and combined, but must be installed strictly according to the above table or the cooling capacity and stability would be decreased.

2. You may substitute the 9K unit with a 7k High Wall unit.

Dimensions

Outdoor Unit

ASUM18HPMULO

Clearances

Outdoor Unit

ASUM18HPMULO