SUBMITTAL DATA SHEET

AUX R32 - Inverter Ducted system Series - AHU36HPV1BI

| Job Name | Location Date |
| --- | --- |
| Purchaser | Engineer |
| Submitted to | For □Reference □Approval □Construction |
| Unit Designation | Schedule # |

AHRI No: 216032395

AHU36HPV1BI

| Specifications |  |  |  |  |
| --- | --- | --- | --- | --- |
| Model | Indoor unit |  |  | AHU36HPV1BI |
|  | Outdoor unit |  |  | AHU36HPV1BO |
| Cooling | Capacity | Rated | Btu/h | 36000 |
|  | Capacity Range | Min-Max | Btu/h | 8500-39500 |
|  | Power Input | Rated | W | 3600 |
| Heating | Capacity at 47℉ | Rated | Btu/h | 38000 |
|  | Capacity Range | Min-Max | Btu/h | 7600-39500 |
|  | Power Input at 47℉ | Rated | W | 3375 |
| Electric Data | Power Supply |  | V~,Hz,Ph | 208/230,60,1 |
|  | Rated Cooling Current |  | A | 15.97 |
|  | Rated Heating Current |  | A | 14.97 |
|  | MCA | Indoor unit | A | 5.7 |
|  | MAX.Fuse | Indoor unit | A | 10 |
| Efficiency | SEER2 |  | (Btu/h)/W | 18.20 |
|  | HSPF2(Region IV) |  | (Btu/h)/W | 10.00 |
|  | EER2 |  | (Btu/h)/W | 10.00 |
|  | COP |  | W/W | 3.30 |
| Indoor Unit | Indoor Air Flow | Hi/Mi/Lo | CFM | 1200/950/790 |
|  | Noise Level | Hi/Mi/Lo | dB(A) | 53/51/49 |
|  | External Static Pressure |  | in.w.g | 0.5(0~1) |
|  | Net Dimension | H | In.[mm] | 49[1245] |
|  |  | W | In.[mm] | 21[534] |
|  |  | D | In.[mm] | 21[534] |
|  | Packing Dimension | H | In.[mm] | 55-1/2[1410] |
|  |  | W | In.[mm] | 24-5/8[625] |
|  |  | D | In.[mm] | 27-3/4[705] |
|  | Weight | Net/Gross | lbs | 132.9/152.1 |
| Pipe | Liquid(O.D.) |  | In.[mm] | 3/8[Ф9.52] |
|  | Gas(O.D.) |  | In.[mm] | 5/8[Ф15.88] |
|  | Max. Length |  | ft[m] | 164[50] |
|  | Max. Height |  | ft[m] | 98[30] |

Submittal Data Sheet - AHU36HPV1BI

| Operation Temperature Range |  | ℉（℃） | 61~90(16~32) |
| --- | --- | --- | --- |
| Ambient Temp Range | Cooling | ℉（℃） | 5~125(-15~52) |
|  | Heating | ℉（℃） | -22~75(-30~24) |
| Remarks: 1.All specifications are subject to change by the manufacturer without prior notice. 2.All units are being tested and comply to AHRI210/240. 3.Sound pressure levels are measured in anechoic chamber. During actual operation, sound pressure level will be higher as a result of room specification condition. 4.Data from AUX lab,30/09/24, Data may change according to test surroundings, AUX reserves right of explanation on data. Connection Wiring | Power Wiring（Indoor） | AWG | 18 |
|  | Signal Wiring | AWG | 22 |

Dimensions

Indoor Unit

AHU36HPV1BI