SUBMITTAL DATA SHEET

AUX R32 - Inverter Ducted system Series - AHU60HPV1AO

| Job Name | Location Date |
| --- | --- |
| Purchaser | Engineer |
| Submitted to | For □Reference □Approval □Construction |
| Unit Designation | Schedule # |

AHRI No: 216030574

AHU60HPV1AO

| Specifications |  |  |  |  |
| --- | --- | --- | --- | --- |
| Model |  |  |  | AHU60HPV1AO |
| Electric Data | Power Supply |  | V~,Hz,Ph | 208/230,60,1 |
|  | Max. Input Consumption |  | W | 7000 |
|  | Max. Current |  | A | 32 |
|  | MCA | outdoor unit | A | 34 |
|  | MAX.Fuse | outdoor unit | A | 50 |
|  | Recommended Breaker Size |  | A | 45 |
| Air Flow Volume |  |  | CFM | 4000 |
| Noise Level |  |  | dB(A) | 60 |
| Outdoor Unit | Net Dimensions | H | In.[mm] | 51-15/16[1320] |
|  |  | W | In.[mm] | 39-13/16[1011] |
|  |  | D | In.[mm] | 15-3/4[400] |
|  | Package Dimensions | H | In.[mm] | 56-11/16 [1440] |
|  |  | W | In.[mm] | 42-1/2[1080] |
|  |  | D | In.[mm] | 16-15/16[430] |
|  | Weight | Net/Gross | lbs | 204.972/224.9 |
| Refrigerant | Charged Volume |  | OZ | 130.51 |
| Pipe | Liquid(O.D.) |  | In.[mm] | 3/8[Ф9.52] |
|  | Gas(O.D.) |  | In.[mm] | 3/4[Ф19.05] |
|  | Max. Length |  | ft[m] | 164[50] |
|  | Max. Height |  | ft[m] | 98[30] |
| Ambient Temp Range |  | Cooling | ℉（℃） | 5~125(-15~52) |
|  |  | Heating | ℉（℃） | 5~75(-15~24) |
| Remarks: 1.All specifications are subject to change by the manufacturer without prior notice. 2.All units are being tested and comply to AHRI210/240. 3.Sound pressure levels are measured in anechoic chamber. During actual operation, sound pressure level will be higher as a result of room specification condition. 4.Data from AUX lab,30/09/24, Data may change according to test surroundings, AUX reserves right of explanation on data. Connection Wiring |  | Power Wiring（Outdoor） | AWG | 8 |
|  |  | Signal Wiring | AWG | 22 |

Dimensions

Indoor Unit

AHU60HPV1AO