## GIIGNL
TSG Survey on Remote or Local Start Up of equipment
| Reply 1 | Reply 2 | Reply 3 | Reply 4 | Reply 5 | Reply 6 | Reply 7 | Reply 8
1. Is the following equipment started locally (i.e. by a (field) operator nearby) or remotely (i.e. from your control room without presence of an operator nearby)? [Low Pressure LNG pumps] | Remotely | Locally | Remotely | Locally | Remotely | Remotely | Remotely | Remotely
1. Is the following equipment started locally (i.e. by a (field) operator nearby) or remotely (i.e. from your control room without presence of an operator nearby)? [High pressure LNG pumps] | Remotely | Locally | Remotely | Locally | Remotely | Remotely | Remotely | Remotely
1. Is the following equipment started locally (i.e. by a (field) operator nearby) or remotely (i.e. from your control room without presence of an operator nearby)? [Submerged Combustion Vaporisers] | Not applicable | Locally | Remotely | Not applicable | Not applicable | Not applicable | Remotely | Remotely
1. Is the following equipment started locally (i.e. by a (field) operator nearby) or remotely (i.e. from your control room without presence of an operator nearby)? [High pressure boil-off gas compressors] | Remotely | Locally | Remotely | Locally | Not applicable | Remotely | Remotely | Remotely
1. Is the following equipment started locally (i.e. by a (field) operator nearby) or remotely (i.e. from your control room without presence of an operator nearby)? [Low pressure boil-off gas compressors] | Remotely | Locally | Remotely | Locally | Remotely | Remotely | Remotely | Remotely
1. Is the following equipment started locally (i.e. by a (field) operator nearby) or remotely (i.e. from your control room without presence of an operator nearby)? [Seawater pumps for Open Rack Vaporisers] | Remotely | Locally | Remotely | Not applicable | Remotely | Remotely | Remotely | Not applicable
1. Is the following equipment started locally (i.e. by a (field) operator nearby) or remotely (i.e. from your control room without presence of an operator nearby)? [Any other equipment] | Remotely | Locally | Remotely | Locally | Remotely | Remotely | Remotely | Remotely
2a). If only local starting, what is the reason for not allowing remote start-up? | TSG Survey on Remote or Local Start Up of equipment Reply 2: Historic reasons but supported by a large experience that point to most of the incidents, leaks, near misses, etc. happen when starting-up LNG/GAS/SW equipments and their defects have to be detected, avoided and reduced when the first seconds after running.; TSG Survey on Remote or Local Start Up of equipment Reply 4: Safety. It is recommended to inspect equipment locally prior to start.; TSG Survey on Remote or Local Start Up of equipment Reply 5: After a major overhaul; TSG Survey on Remote or Local Start Up of equipment Reply 6: We don't have any equipment operated local.
2b). If only local starting, did you ever consider to start (part) of the above mentioned equipment remotely and what is the reason for not doing so? | TSG Survey on Remote or Local Start Up of equipment Reply 2: Only in case of non-critical equipment (Nitrogen, Air system, low voltage machines, ...); TSG Survey on Remote or Local Start Up of equipment Reply 4: Safety.; TSG Survey on Remote or Local Start Up of equipment Reply 5: All automatic; TSG Survey on Remote or Local Start Up of equipment Reply 6: We don't have any equipment operated local.
3. In case of remote starting of (part of) the above mentioned equipment, do you have additional measures in place? | Check by operator after start-up, Additional Measurements, Additional alarms, Trending, CCTV system | Check by operator after start-up, Trending, Monitored by CCTV (Closed Circuit TV) | Check by operator after start-up, Trending, local checking at the same time |  | Check by operator after start-up, Additional Measurements, Additional alarms, Trending | Check by operator after start-up, Additional Measurements, Additional alarms, Trending | Check by operator after start-up, Remote start-up with systematic presence of field operator locally | Check by operator after start-up, Trending
4. Any other comments | TSG Survey on Remote or Local Start Up of equipment Reply 6: Nothing; TSG Survey on Remote or Local Start Up of equipment Reply 7: Field operator to check absence of leaks, abnormal noises,...at start-up