## nov15
Unique ID | 1273609100 | 1273855032 | 1274382945 | 1274612422 | 1275417389 | 1277110750 | 1277832071 | 1280753659 | 1283358517 | 1285769359 | 1286651779 | 1286975434 | 1287194932 | 1287283992
a. How many and what type of flares / vent stacks do you have? | 1 flare per terminal | One elevated flare / No vent | One flare | One heated vent on each tank (2 tanks). One (unheated) discretionary vent on each tank (2 tanks). One KO pot that vents to a ground vent stack. | Only vent stacks | Two conventional flares mounted side by side on a single derrick structure | 1 type | Senboku 1 Flare x 1、 | Vertical Flare with pilots (always working) and water seal | 1 Flare and 1 Vent (Only for the old Tanks) | 2 x vent stack | 1 | In total, the company's four LNG terminals have nine flare stacks and seven vent stacks. All types are Elevated Flare. | 2 Water Boiler as vent stack heater (1 main, 1 spare)
b. Are these flares / vent stacks equipped with flare pilot burners? | Yes | Yes | Yes | No | No | Yes | Yes |  | Yes | Yes | No | Yes | Yes | No
c. If pilot burners, are these | continuously ignited, | [8 empty] | only active when flaring occurs
d. What type of fuel do you use for the pilot (NG, LPG, H2, Other..). | NG | NG with LPG as back-up | GN | No Pilots, No Flares. Vents only. |  | NG and Propane as back-up | LPG, NG |  | NG | NG | n/a | LPG on start-up | NG | NG
If no flares or no flare pilot burners, the rest of the survey can be ignored. In the other case, please continue with the following sections. | I continue with the following questions | I continue with the following questions | I continue with the following questions | No flare, submit my form now |  | I continue with the following questions | I continue with the following questions |  | I continue with the following questions | I continue with the following questions | No flare, submit my form now | I continue with the following questions | I continue with the following questions | No flare, submit my form now
2. Have you implemented or conducted research on any measures to reduce emissions from flare pilot burners? | Yes | No | No |  |  | Yes | No |  | Yes No | Yes |  | Yes | No
Please, specify | Implement a system that would ignite the flare in case of necessity by electronic ignition. A ballistic pellet ignition would also be implemented in case the main system wouldn't work. |  |  |  |  | Engineering studies. Solution screening to optimize emissions from flare pilots. |  |  | Deflectors | Using H2 instead of NG under study |  | Nitrogen (N2) is being used based on the design condition of flare tip and burner instead of NG.
What was the percentage reduction in CO2 emissions achieved through these measures? | 100% |  |  |  |  | No achievement yet. Only studies. But solutions identified could offer a reduction from 50% to 100% |  |  |  | Under study |  | Minus 8338 tCO2 /yr
3. Have you considered or implemented any alternatives to Front Flame Generators, such as electronic ignition or ballistic pellet ignition? | Yes | No | Yes |  |  | Yes | Yes |  | No | No |  | No | No
Please list the alternative(s) implemented | We have been considering implementing a system that would ignite the flare in case of necessity by electronic ignition. A ballistic pellet ignition would also be implemented in case the main system wouldn't work. |  | Install electronic ignition, we have a Pellet Ignition system already install. |  |  | Electronic ignition already present as a back-up ignition system. Other considerations studied :Low consumption pilots, pilots on demand system (ignition only when needed), Ballastic system (disregarded solution) | FFG and HEI
What were the determining factors in choosing the specified alternative(s)? |  |  | to have redundant system, due to we want to have the pilot off all the time. |  |  | No decision taken yet. Determining factors would be the following : CAPEX, Safety, Reliability, Implementation (flare stoppage during works) , Emission reduction performance. | As per original design
4. How do the following factors affect the reliability of the ignition in the alternative systems you’ve implemented? (Extreme weather conditions e.g. rain, wind, Significant variations in flared gas flow, Changes in gas compositions e.g. variation in high nitrogen content) | The system hasn't been implemented. | N/A | We will keep the actual flame generator system and upgrade the actual Peller system. |  |  | All solutions identified are suitable with extreme listed examples. | No major reliability issues. |  | At first we had problems with the strong winds in the area, which led us to increase the pressure on the flare pilots to prevent them from turning off, resulting in greater NG consumption, which is why a deflector protection for the pilot was installed, which allows it to work at lower pressure, reducing NG consumption and maintaining the reliability of the pilot. | The flare pilots are always active, the gas flow is regulated to be low enough to avoid resource waste but steady enough to prevent the flame from going out. |  | Terminal ignition system reliability is ensured by Energy Efficient Utility Flare Tip (EEF-U) which maintains stability/burn back/Flame pull down | We have not implemented an alternative system.
5. How do you manage or prevent unignited methane/natural gas venting via your terminal’s flaring/venting systems? | Today our flares have pilot burners. | Pilot are always on. | Having a tank pressure we early alarms. Having a good maintenance and test plan of pellet, flame generator y propene system. Having a pop-up indication that advise the operator that the flare have the pilot off and need to be on. |  |  | For the time being, pilots are constantly lit. Methane venting is near zero. Unburnt emissions are estimated via stoechiometric combustion calculation. | Flare Take-in Logic - To take on-spec NG for reloading and GUCD operations. |  | At the moment, there is no action on the flare. In the case of the necessary venting, we have identified the type of intervention required for maintenance and that by design for its execution a venting of a line or equipment must be carried out. We have identified all these activities by system to execute them simultaneously and reduce the impact. | To keep pilot active, the gas flow rate is carefully regulated to maintain a minimal yet steady flame, sensors that monitor flame presence and gas flow LDAR campaign includes monitoring unburned compounds with OGI camera (optical gas image) |  | Controlled reliefs are recovered and reused in normal scenario. Uncontrolled reliefs are routed to Flare/ Vent only in case of any emergency. | In consideration of the ignition failure of the pilot burner, the procedure is to dissipate the gas after the pilot burner is ignited. In addition, in order to improve the reliability of the equipment, three pilot burners are provided in the flare burner. As for vent dissipation, we operate it as little as possible.
6. Have there been any safety or environmental risks or impacts observed or anticipated due to the implementation of alternative ignition systems, such as methane emissions, impact on explosive zones/atmospheres, noise…? |  | NO alternative ignition systems have been considered so far. | We are now working with the vendor for implementation |  |  | The studies conducted for optimizations covered several scenarii : (1) No pilot and methane emissions - dispersion study , (2) Late ignition of pilot and subsequent flare fire. Both solutions concluded on no safety impact for personnel. | No. |  | No | not using a pilot continuously in flares that burn natural gas can indeed increase the risk of methane emissions |  |  | We have not implemented an alternative system.
7. What has been the impact of implementing alternative ignition systems on the original flaring system (modification cost), maintenance requirements and operational expenses? | The system hasn't been implemented. | NO alternative ignition systems have been considered so far. | We are now working with the vendor for implementation |  |  | Except CAPEX due to modification costs and necessary terminal shutdown to implement the new elements, no significant impact (OPEX) is identified. | It was implemented as per design |  | no impact. | Using H2 instead of NG under study |  | Cost inclusive of Operation/ Maintenance/Modification/ Time and it depends on type of alternative. | We have not implemented an alternative system.
8. Have there been any noticeable differences in costs/time consumption associated with the use of these alternatives? | The system hasn't been implemented. | NO alternative ignition systems have been considered so far. | We are now working with the vendor for implementation |  |  | Project on going. No FID taken at this stage. | No. It was implemented as per design |  | no. | Under study |  | reply 7 | We have not implemented an alternative system.