Drinking Water Quality and Compliance

Town Short Form – A Template for Annual Notice to Consumers

(Note:  This short form may be used for communities or waterworks serving a population of less than 5000).

Introduction

The Water Security Agency and the Ministry of Environment requires that at least once each year waterworks owners provide notification to consumers of the quality of water produced and supplied as well as information on the performance of the waterworks in submitting samples as required by a Minister’s Order or Permit to Operate a waterworks.  The following is a summary of the Special Service Area of Sceptre in the R.M. of Clinworth No. 230’s water quality and sample submission compliance record for the year 2025.  This report was completed on January 23, 2026.  Readers should refer to Water Security Agency’s Municipal Drinking Water Quality Monitoring Guidelines, June 2015, EPB 502 for more information on minimum sample submission requirements and the meaning of type of sample.  Permit requirements for a specific waterworks may require more sampling than outlined in the department’s monitoring guidelines.  If consumers need more information on the nature and significance of specific water tests, for example, “what is the significance of Selenium in a water supply”, more detailed information is available from:  http://www.hc-sc.gc.ca/ewh-semt/pubs/water-eau/index_e.html 
.

Water Quality Standards 

Bacteriological Quality



Regular Samples
Regular Samples
  # of Positive Regular

Parameter/Location
Limit


Required

Submitted
  Submitted (%)

Total Coliform 

0 Organisms/100 mL

12

12

0 (0%)
E. coli


0 Organisms/100 mL

12

12

0 (0%)
Water Disinfection – 

Chlorine Residual in Distribution System for Test Results Submitted with Bacteriological Samples


Minimum
Total Chlorine
Free Chlorine
# Tests
# Tests
# Adequate

Parameter
Limit
Residual Range
Residual Range
Required
Submitted
Chlorine (%)
Chlorine
0.1 mg/L free OR


Residual
0.5 mg/L total
0.87 – 1.66
0.59 – 1.20
12
12

12(100%)

Water Disinfection - Free Chlorine Residual for Water Entering Distribution System from Waterworks Records-From Water Treatment Plant Records



Test Level
# Tests                # Tests Not Meeting

Parameter
Limit (mg/L)
Range
Performed          Requirements

Free Chlorine Residual
at least 0.1
0.19 – 2.11
365
0
A minimum of 0.1 milligrams per litre (mg/L) free chlorine residual is required for water entering the distribution system.  Tests are normally performed on a daily basis by the waterworks operator and are to be recorded in operation records.  This data includes the number of free chlorine residual tests performed, the overall range of free chlorine residual (highest and lowest recorded values) and the number of tests and percentage of results not meeting the minimum requirement of 0.1 mg/L free chlorine residual.

Turbidity – From Water Treatment Plant Records

Parameter
Limit
Test Level
# Tests Not Meeting
Maximum
# Tests           # Tests

# Tests


(NTU) 
Range
Requirements
Turbidity (NTU)
Required        Performed
Performed

Turbidity
1.0
0.07 – 0.92
0
0.92
365                 365
Chemical – Health Category 

All waterworks serving less than 5000 persons are required to submit water samples for SE’s Chemical Health category once every 2 years.  The Chemical Health category includes analysis for arsenic, barium, boron, cadmium, chromium, fluoride, lead, nitrate, selenium and uranium.

The last sample for Chemical Health analysis was submitted on January 13, 2025.  Sample results indicated that the provincial drinking water quality standards were not exceeded.  

Limit
Limit
Sample
# Samples

Parameter
MAC(mg/L)
IMAC (mg/L)
Result(s)
Exceeding Limit

Arsenic
0.010

0.0012


   * Results expressed

Barium
1.0

0.0082

as average values 

Boron

5.0
0.3


      for communities or
Bromate
0.01

N/A


      waterworks that

Cadmium
0.005

<0.00015


      fluoridate drinking
Chlorate
1.0

N/A


      water supplies or

Chlorite
1.0

N/A


      those with elevated

Chromium
0.05

<0.00019


      concentrations of
Fluoride (avg*)
1.5

0.21


      fluoride or nitrates.
Lead
0.01

0.00030      
Nitrate (avg.*)
45.0

<0.2      
Selenium
0.01

<0.00113
Uranium
0.02

0.0067
General Chemical 



Aesthetic 

Sample Results
# Samples  # Samples


Parameter
Objectives * (mg/L)
(average)
Required
Submitted 

Alkalinity
500
490
Bicarbonate
No Objective
598


Calcium
No Objective
171
 

Carbonate
No Objective
0
 

Chloride
250
19.7        

Conductivity
No Objective
1618


Hardness
800
818
Magnesium
200
95
PH
No Objective
7.6
Sodium
300
108
Sulphate
500
477.0
Total dissolved     


Solids                   1500
                         1475
All waterworks serving less than 5000 persons are required to submit water samples for SE’s General Chemical category once every two years if a ground water source and once per three months every second year if a surface water or blended surface/groundwater source.  The General Chemical category includes analysis for alkalinity, bicarbonate, calcium, carbonate, chloride, conductivity, hardness (as CaCO3), magnesium, sodium, sulphate and total dissolved solids.

The last sample for General Chemical analysis was required in 2025 and submitted on January 13, 2025.   Sample results indicated that there were no exceedences of the provincial aesthetic objectives for the General Chemical category 

*Objectives apply to certain characteristics of or substances found in water for human consumptive or hygienic use.  The presence of these substances will affect the acceptance of water by consumers and/or interfere with the practice of supplying good quality water.  Compliance with drinking water aesthetic objectives is not mandatory as these objectives are in the range where they do not constitute a health hazard.  The aesthetic objectives for several parameters (including hardness as CaCO3, magnesium, sodium and total dissolved solids) consider regional differences in drinking water sources and quality.

More information on water quality and sample submission performance may be obtained from:

R.M. of Clinworth No. 230
Box 120
Sceptre, SK  S0N 2H0  
PH. 306-623-4229  FAX 306-623-4229  
rm230@yourlink.ca
[image: image1.jpg]Saskatchewan
Ministry of
Environment




                                                                          [image: image2.jpg]Water Securtty
Agency

O



                   

[image: image1.jpg][image: image2.jpg]