CampbellRhea “Signature” Oak Specification

SECTION 12300

MANUFACTURED CASEWORK

To display hidden notes to Specifier: Click on Office logo (upper left corner); click on Word Options (bottom right); left menu, click on Display; under ‘Always show these’ select ‘Hidden Text’

** NOTE TO SPECIFIER ** ICI/CampbellRhea™; laboratory casework, furniture, fixtures, countertops, equipment and fume hoods.

This section is based on the products of CampbellRhea™, manufactured by ICI (Institutional Casework Incorporated), located at:
1865 Highway 641 North 
Paris, TN 38242-8814
Tel: 731-642-4251
Fax: 731-642-4262
Email: rjohnson@iciscientific.com
Web: www.iciscientific.com

ICI’s CampbellRhea™ Casework has been certified by an independent testing facility to meet or exceed the performance and resistance standards of SEFA-8W. CampbellRhea (ICI) provides customers with a 3-year warranty. CampbellRhea is certified for chain-of-custody by SmartWood™ and recognized in accordance with the principles and criteria of the Forest Stewardship Council™ (FSC™). As a chain of custody provider CampbellRhea can be considered for contribution to the LEED™-NC Certification Process. ICI is a certified participant in AWI’s Quality Certification Program (AWI/QCP). All SEFA-8W™, FSC™, LEED™-NC or AWI/QCP certifications must be specified.

ICI reserves the right to modify, change or delete it’s product offerings without notice.

- GENERAL

  - SECTION INCLUDES

    - Fixed modular casework furniture with finished interiors.

    - Countertops.

    - Fixtures.

    - Sinks, faucets, and plumbing accessories.

    - Electrical fixtures and accessories.

    - Fume hoods.

    - Utility-space closure panels between base cabinets and at exposed ends of utility spaces.

    - Utility-space framing at backs of base cabinets and between backs of base cabinets.

    - Related equipment.

  - RELATED SECTIONS

    - Section 06100 - Rough Carpentry:  Framing and blocking in walls, floors and ceiling to support equipment.

    - Section 09650 - Resilient Flooring: base for casework including floor cabinets and table legs.

    - Section 15050 - Basic Mechanical Materials and Methods: Connections for drain lines, service piping, vents, re-vents, in-line vacuum breakers, special plumbing fixtures, traps and tailpieces to service fixtures.

    - Section 16050 - Basic Electrical Materials and Methods: Connections for electrical service lines, wire and conduit to service fixtures.

  - REFERENCES

    - ADA (ATBCB ADAAG): Americans with Disabilities Act Accessibility Guidelines.

    - ANSI/AIHA 9.5: American National Standard for Laboratory Ventilation.

    - ANSI/ASHRAE 110: Method of Testing Performance of Laboratory Fume Hoods.

    - ANSI 2358.1: Minimum Performance Requirements for Emergency Showers.

    - ASTM A167: Standard Specification for Stainless and Heat-Resisting Chromium-Nickel Steel Plate, Sheet, and Strip.

    - ASTM A 666: Standard Specification for Annealed or Cold-Worked Austenitic Stainless Steel Sheet, Strip, Plate, and Flat Bar.

    - Architectural Woodwork Institute (AWI):  Quality Standards.

    - FS W-C-596: Electrical Power Connector, Plug, Receptacle, and Cable Outlet.

    - NEMA WD 1: General Color Requirements for Wiring Devices.

    - NEMA WD 6: Devices-Dimensional Requirements.

    - NEMA LD 3: High Pressure Decorative Laminates.

    - NFPA 30: Flammable and Combustible Liquids Code.

    - NFPA-45: Standard for Fire Protection for Laboratories Using Chemicals.

    - OSHA 29-CFR-1910.1450: Occupational Exposure to Hazardous Chemicals in Laboratories.

    - SEFA 1: Laboratory Fume Hoods - Recommended Practices.

    - SEFA 7: Laboratory and Hospital Fixtures--Recommended Practices.

    - SEFA 8: Laboratory Furniture--Casework, Shelving and Tables--Recommended Practices.

    - UL 498: Attachment Plugs and Receptacles.

    - UL 1805: Laboratory Hoods and cabinets, where applicable.

    - FSC: Forest Stewardship Council.

    - CARB: California Air Resources Board.

    - “American Made”: Casework wholly manufactured and assembled in USA.

  - SUBMITTALS

    - Submit under provisions of Section 01300.

    - Manufacturer's data sheets on each product to be used, including:

      - Test reports certifying that the casework finish complies with SEFA-8 standards for chemical and physical resistance performance requirements.

      - Performance test reports from an independent testing lab on each specified top material.

      - Preparation instructions and recommendations.

      - Storage and handling requirements and recommendations.

      - Installation methods.

    - Shop Drawings: Include plans, elevations, sections, details, and attachments to other work.

      - Indicate locations of blocking and reinforcements required for installing laboratory casework.

      - Indicate locations and types of service fittings, together with associated service supply connection required.

      - Include details of utility spaces.

      - Include indicators of exposed conduits, if required, for service fittings.

      - Indicate locations of and clearances from adjacent walls, doors, windows, other building components, and other laboratory equipment.

      - Include coordinated dimensions for laboratory equipment specified in other Sections.

    - Certificate of Origin: Manufacturer must supply with first submittal, an example of their Certificate of Origin declaring casework is wholly manufactured and assembled specifically in the United States, including city, county, and state locations. A notarized Certificate of Origin must be provided with closeout documents.

    - Selection Samples:	For each finish product specified, one complete set of color chips representing manufacturer's full range of available colors and patterns.

      - One set of samples indicating full range of finishes for countertop specified.

      - One set of casework samples indicating full range of finishes for casework specified.

    - LEED Submittals: Provide documentation affirming that specific products listed in this section contribute to the following LEED Credits:

      - MR Credit 4: Recycled Content.

      - MR Credit 5: Regional Material.

      - MR Credit 6: Rapidly Renewable Materials.

      - MR Credit 7: Certified Wood.

      - IEQ Credit 4.1: Low-emitting Materials – Adhesives & Sealants.

      - IEQ Credit 4.2: Low-emitting Materials – Paints & Coatings.

      - IEQ Credit 4.4: Low-emitting Materials – Composite Wood & Agrifiber Products.

  - QUALITY ASSURANCE

    - Manufacturer Qualifications: Not less than 5 years experience in the actual production of specified products. Casework shall be wholly manufactured and assembled in the USA: i.e. “American Made”.

    - Installer Qualifications: Firm with 5 years experience in installation or application of systems similar in complexity to those required for this Project, plus the following.

      - Authorized distributor of manufacturer.

    - Mock-Up:  Provide a mock-up for evaluation of fabrication techniques and application workmanship.

      - Installation in area designated by Architect.

      - Do not proceed with remaining work until installation is approved by Architect.

      - As selected and required by Architect's request for mock-up: Install base cabinet with drawer and cupboard, one adjustable shelf, hinged door and applicable hardware. Wall case with adjustable shelf, hinged door and applicable hardware. Tall case with adjustable shelves, fixed center shelf, hinged door and applicable hardware, including a 3-point latching system.

  - DELIVERY, STORAGE, AND HANDLING

    - Store products in manufacturer's unopened packaging until project conditions are ready for installation.

  - PROJECT CONDITIONS

    - For delivery and installation of laboratory casework and equipment, building conditions shall comply with AWI Standard 10.5 and 10.6 be as follows:

      - Flooring required to be placed under casework and equipment installed.

      - Wood or metal blocking (wall grounds) installed within partitions to allow for immediate installation upon delivery.

      - Heating and air conditioning systems providing consistent temperature and humidity conditions to comply with by AWI Standard Section 2.

      - Relative humidity not less than 40 percent, nor more than 60 percent.

      - Temperatures not less than 65 degrees F (18 degrees C) and not greater than 80 degrees F (27 degrees C) in areas of casework and equipment installation.

      - Overhead mechanical, electrical and plumbing rough-in work is complete.

      - Wet operations complete prior to delivery.

      - Ceiling grids (with or without ceiling tiles), overhead soffits, ductwork and lighting installed.

      - Painting complete.

  - WARRANTY

    - Casework Manufacturer Warranty: 3 years from date of delivery. Warranty is for the conditions indicated below, and when notified in writing from Owner, manufacturer shall promptly investigate and address said deficiencies.

      - Defects in materials and workmanship.

      - Deterioration of material and surface performance below minimum SEFA 8 standards as certified by independent third party testing laboratory.

      - Within the warranty period, we shall, at our option, repair, replace, or refund the purchase price of defective casework.

    - Casework manufacturer shall be notified immediately of defective products, and be given a reasonable opportunity to inspect the goods prior to return. Casework manufacturer will not assume responsibility, or compensation, for unauthorized repairs or labor. Casework manufacturer makes no other warranty, expressed or implied, to the merchantability, fitness for a particular purpose, design, sale, installation, or use, of casework; and, shall not be liable for incidental or consequential damages, losses of or expenses, resulting from the use of their products.

      - The warranty with respect to products from another company sold by the casework manufacturer is limited to the warranty extended by that other company.

    - Casework manufacturer shall provide, with close-out documents, a Certificate of Warranty for products provided.

- PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturer: CampbellRhea, which is located at: 1865 N. Market St.; Paris, TN 38242; Tel: 731-642-4251; Fax: 731-642-4262; Email: To request information   sales@iciscientific.com; Web: www.iciscientific.com

    - Product Designations:  Drawings indicate sizes and configurations of laboratory casework by referencing designated manufacturer's catalog numbers.  Other manufacturers' laboratory casework of similar sizes, similar door and drawer configurations, and complying with the Specifications, including certification to SEFA-8 standards for construction and chemical resistance, may be requested for approved substitution. Requests for substitutions will be considered in accordance with provisions of Section 01600.  No exceptions will be made for casework that is not wholly manufactured and assembled in USA: i.e. “American Made”.

  - APPLICATIONS/SCOPE

    - Casework Group: Manufacturer shall offer an integrated product line serving the user function indicated with a coordinated design, supply and installation of casework, equipment, work surfaces, and accessories:

      - General casework.

      - Technology.

      - Laboratory.

      - ADA compliant.

      - Life skills.

      - Art

      - Photographic

      - Music

      - Shop.

  - CONSTRUCTION

    - Wood veneer on plywood core: CampbellRhea Casework.

    - Cabinet Finish, Interiors and Exteriors Match Finished:

      - Wood Species:  Oak.

      - Finish:  #101 Briar finish.

    - Drawer and Door Styles:

      - Signature Drawer and Door Styling: Both door and drawer fronts are 13/16 inch (20.6 mm) thick and have a slight radius to the squared edges. Drawers are solid hardwood with horizontal grain. Doors have particleboard core with internal hardwood stiles and rails and vertical grain wood veneer face and back.

    - Door and Drawer Hardware Style:

      - Drawer and door pulls:

        - AL-2: Extruded aluminum rod design.

      - Sliding wood door pulls:

        - RS -1: Recessed, metal finger grip is nickel-plated pull.

      - Sliding glass door pulls:

        - RS-2: Recessed, metal two-piece, screw together style with a bright chrome finish.

      - Hinges:

        - SS-1:   Heavy-duty, institutional type, 5-knuckle hospital tipped, made from 0.083 inch (2 mm) thick stainless steel. Hinge is semi-concealed, 2 1/2 inches (64 mm) high and has off-set wings; each wing has three screw holes for the door leaf and three screw holes for the case leaf, two of which are slotted for adjustability. Hinges are attached with Euro screws.

      - Latching Handle:

        - CP: Latching handle CP LH-1 is chrome plated, 4 1/4 inches (108 mm) long and streamline in design. Handle operates with 1/4 turn. Double door cases have latching handles on the right door and dummy handles on the left door. A three point latching system provides a positive engagement at the top and bottom of the door with tapered aluminum rods, which pull the door snug when they engage plastic strike plates. The rods are 5/16 inch (8 mm) in diameter and move in nylon guides attached to the back of the door. The middle of the door is secured by a latch plate, which engages the side of the case, or latches behind the left door on cases with double doors.

      - Locking Handle:

        - CP: Chrome plated locking handle is a latching handle with a lock mechanism incorporated into the handle head. On double door cases, the left door has a dummy handle, and the right door has the locking handle. Lock is laboratory grade with a 5-disc tumbler mechanism with a brushed chrome face. Tumblers and keys are brass, while the plug and cylinder is die cast zinc alloy. There are 500 key changes standard. Locks are keyed differently, master keyed and furnished with 2 keys per lock. Locks and corresponding keys are alpha-numerically coded for a quick match.

      - Locks: Removable core standards:

        - CP: Lock CP SL-1 is laboratory grade, cylinder cam lock, with a 5-disc tumbler mechanism with a chrome plated face. Tumblers and keys are brass, while plug and cylinder is die cast zinc alloy.  A 180-degree turn of the key moves the lock cam into, or out of, a slot cut to receive it. There are 500 key changes standard. Locks are keyed differently, master keyed and furnished with 2 keys per lock.  Locks and corresponding keys are alpha-numerically coded for a quick match.  Lock CP SL-1 is equipped with a removable core, keying control. With the use of a control key, the key core of the lock assembly can be removed and a new key core inserted, changing the entire locking system in a matter of minutes. Key cores can be held out of the lock assembly until the project is completed, removing the security risk of lost or stolen keys during installation and construction. Casework manufacturer can provide control keys and replacement cores as required. Locks are furnished only when specified.

8.	Drawer Slides:

a.       Drawer slides DS-1: Epoxy powder coated, cold rolled steel, 					bottom/side mount, heavy-duty with a 100 lbs (45 kilograms) load 				capacity. They are equipped with heavy-duty, nylon rollers for smooth 				effortless operation. Slides are self-closing; and have automatic 					positive stop to prevent drawer's accidental removal, but allow for quick 				removal without tools.

9.	File Drawer Slides:

a.	File drawer slides FD-1: Zinc plated, cold rolled steel, heavy-duty, side 				mounted, and have a 125 lbs (56.25 kg) load capacity. They are 					equipped with heavy-duty, precision ball bearings, for smooth 					effortless operation. Slides are full extension with a positive stop, and a 				trigger finger release..

2.4	MATERIALS

    - Oak Lumber:  Grade FAS or better, air-dried and kiln dried to 6 percent moisture content, then tempered to 7 to 8 percent prior to fabrication.  Lumber exposed to view, is free of stains, splits, shakes, season checks and other similar defects. Other hardwoods are grade FAS or better, air dried to 6 percent moisture content, then tempered to 7 to 8 percent prior to fabrication. Other hardwoods are used in semi-exposed, or unexposed, areas and comply with NHLA grading for FAS or better lumber.

    - Oak Plywood:  Plywood is plain sliced, book-matched Oak, select grade A-1, cross-banded, and has a veneer core. The 1 inch (25 mm) plywood is minimum of 9-ply, 3/4 inch (19 mm) plywood is a minimum of 7-ply, 1/2 inch (12 mm) is a minimum of 5 ply, 1/4 inch (6 mm) is minimum of 3 ply, and 3/32 inch (2.4 mm) is 3-ply. Other hardwood plywood is sound grade, has a solid core and is suitable for semi-exposed or unexposed areas. All plywood shall be CARB Phase 2 compliant.

    - Hardboard used in drawer bottoms and unexposed backs, consists of super-refined wood 	fibers and chips, highly compressed into a hard, dense, 1/4 inch (6 mm) thick, 	homogeneous sheet, faced with a color coordinated (to cabinet finish) melamine on the exposed face. Natural finish selections have a white melamine face. All other finish colors have a flat, color coordinated melamine face. Physical properties: Average MOR is 5,000 lbs/sq inches (3.5 kgf/sq mm); density is 48 lbs/cu ft (0.6 kg/cum); and MOE of 500,000 psi (350 kgf/sq mm). All hardboard shall be CARB Phase 2 compliant.

2.5	FABRICATI0N

A.	Units and configurations designated for accessibility by users shall comply with 		ATBCB ADAAG (ADA standards).

B.	Design, material and construction of casework, shelving and tables shall comply 		with SEFA 8 performance and resistance standards.

C.	Electrical Components, Devices, and Accessories:  Listed and labeled as defined in 		NFPA 70, Article 100, by a testing agency acceptable to authorities having 			jurisdiction, and marked for its intended use.

D.	Base cabinets have a 2 1/4 inches (57 mm) by 1 inch (25 mm), solid hardwood 		horizontal front top frame member and 2 1/8 inches (54 mm) by 1 inch (25 mm), 		solid hardwood horizontal rear and side top frame members. Front intermediate rails 		are 3/4 inch (19 mm) by 2 1/2 inches (64 mm) solid wood. Back intermediate rails 		are furnished only when drawer separators are specified. Exposed exterior backs 		are 3/4 inch (19 mm) plywood. Backs are 1/4 inch (6 mm) finished plywood in 			cabinets with exposed interiors; and, in cabinets with unexposed interiors, backs are 		1/4 inch (6 mm) thick hardboard with melamine face, color coordinated to the interior 		stain. Exposed end panels are 3/4 inch (19 mm) plywood. Unexposed end panels 		are 3/4 inch (19 mm) hardwood plywood. End panels with unexposed interior and 		unexposed exterior are 3/4 inch (19 mm) hardwood plywood. Bottom, shelves, and 		dividers in cabinets with exposed interiors are 3/4 inch (19 mm) plywood; with 			unexposed interiors is 3/4 inch (19 mm) hardwood plywood. If cabinet exceeds 36 		inches (914 mm) in width, shelves shall be 1inch (25mm) thick. Exposed edges of 		front top horizontal frame and intermediate rail members; end panels, bottom, 			shelves, and dividers are edged with 1/8 inch (3 mm) solid wood. Drawer 			separators, furnished only when specified, are 1/4 inch (6 mm) thick hardboard with 		wood grained melamine face.

E.	Cabinet construction is bored, doweled, dadoed, glued and screwed construction. 		Cabinets are enclosed without the use of common partitions. A full horizontal, 			mortise, tenon and glued, top frame is bored, doweled, glued, and reinforced with 		six (6) screws into the cabinet. Intermediate front rails and bottom rear horizontal 		parting rails are provided as required. Separators, where specified, are let into 			routed intermediate rails. Backs are recessed and encapsulated into dadoed end 		panels then screwed into the top and bottom case members. A standard enclosed 		toe space, 2-1/4 inches (57 mm) by 4 inches (102 mm) high, is provided, with toe 		rail bored, doweled and glued to end panels; however, casework cabinets, when in a 		library assembly such as a circulation desk, will have an enclosed toe space 2-1/4 		inches (57 mm) deep by 6 inches (152 mm) high. Shelves are supported on heavy-		duty, laboratory grade, twin pin plastic shelf clips, which fit into two double rows of 		holes drilled 1-1/4 inches (32 mm) on centers, in the case end panels for maximum 		shelf adjustability.

F.	Construction - Wall and Upper Cases:  Wall and upper cases have a 1 inch (25 mm) 		plywood top and bottom panel. Adjustable shelves are 1 inch (25 mm) finished 		plywood in cases with exposed interiors and 1 inch (25 mm) hardwood plywood in 		cases with unexposed interiors. Backs are 1/4 inch (6 mm) finished plywood in 		cabinets with exposed interiors; and, in cabinets with unexposed interiors, backs are 		1/4 inch (6 mm) thick hardboard with melamine face, color coordinated to the interior 		stain. End panels in cabinets with exposed interiors are 3/4 inch (19 mm) finished 		plywood; end panels in cabinets with unexposed interiors are 3/4 inch (19 mm) 		hardwood plywood. Exterior hanger rails are 4 inches (102 mm) by 3/4 inch (19 mm) 		hardwood plywood.

G.	Construction - Tall Cases: Top panels in tall cases with exposed interiors are 1 inch 		(25 mm) hardwood plywood; tall cases with unexposed interiors have top panels of 		1 inch (25 mm) plywood.  Bottom panels in tall cases with exposed interiors are 3/4 		inch (19 mm) hardwood plywood; and unexposed interiors have 3/4 inch (19 mm) 		plywood. Interiors, whether exposed or unexposed, are stain color matched to the 		exterior finish. Adjustable shelves are 1 inch (25 mm) thick hardwood plywood if 		exposed; 1 inch (25 mm) plywood if unexposed. Shelves are edged with 1/8 inch (3 		mm) solid hardwood edging. Backs are 1/4 inch (6 mm) finished plywood in cabinets 		with exposed interiors; and, in cabinets with unexposed interiors, backs are 1/4 inch 		(6 mm) thick hardboard with melamine face, color coordinated to the interior stain.		End panels in tall cases with exposed end panels have 3/4 inch (19 mm) hardwood 		plywood. End panels in cases with unexposed end panels have 3/4 inch (19 mm) 		plywood. All exposed edges of hardwood plywood components and plywood 			components are edged with 1/8 inch (3mm) solid hardwood edging. Tall cases have 		two exterior hardwood plywood cross rails, 4 inches by 3/4 inch (102 mm x 19 mm). 		Tall cases are rigidly constructed, integral units with the strongest, most advanced 		joinery methods utilized of bored, doweled, dadoed, glued and screwed 				construction. Each case is completely enclosed without the use of common 			partitions and has flush construction with overlapping doors to provide a dust 			resistant interior. The top panel is bored, doweled and glued into end panels; and 		the bottom panel is bored, doweled and glued into end panels and glued and 			screwed to the back. Additional back cross rails are provided as required. Backs are 		recessed and encapsulated into dadoed end panels and screwed to the top and 		bottom tall case members. An enclosed toe space 2-1/4 inch by 4 inches (57 mm by 		102 mm) is provided with toe rail securely bored, doweled and glued to end panels 		and bottom panel. Adjustable shelves are supported on heavy-duty laboratory 			grade, twin pin plastic shelf clips, which fit into two rows of holes drilled 1-1/4 inches 		(32 mm) on centers in the end panels, for maximum shelf adjustability.

H.	Drawer front is 13/16 inch (20.6 mm) thick.  Squared edged styles drawer faces are 	screwed to the face of a full drawer box. Drawer box front, sides and back are 1/2 	inch (12 mm), 9-ply laminated hardwood plywood, FSC 100% and CARB Phase 2 	compliant. Drawer bottom is 1/4 inch (6 mm) thick hardboard with white melamine face. All four corners of the drawer are dovetailed and glued. The top edges of drawer box are radiused. Drawer bottom is let in on four sides, and securely glued underneath with a continuous bead of glue around the perimeter of the drawer bottom. In cabinets 24 inches (610 mm) or less in width, drawers have one pull. In cabinets over 24 inches (610 mm) wide, drawers have two pulls.

I.	Construction - Hinged Doors:

      - Hinged solid doors 48 inches (1219 mm) or less in height, 3/4 inch (19 mm) thick and overlap the opening on all sides. Doors have one pull. Door has two heavy duty, institutional type, and 5-knuckle hinges. Doors are secured by a friction roller catch and a metal strike plate.

      - Hinged solid doors, over 48 inches (1219 mm) in height, are 3/4 inch (19 mm) thick and overlap the opening on all sides. Single doors and right door of double doors have a latching handle. A three point latching system provides single doors and right door of double doors positive engagements at the top and bottom of the door with tapered aluminum rods, which engage plastic, strike plates and pull the door snug. The rods are 5/16-inch (8 mm) in diameter and move in nylon guides attached to the back of the door. The middle of the door is secured by a latch plate, which engages the side of the case, or latches behind the left door on cases with double doors and securely hold the door shut. Right door of double doors lap over the machined integral astragal on left door in lipped styles; square edged styles have an applied astragal on the left door. Plastic laminate style doors have particleboard core, and no astragal. Doors have four hinges. On double doors left door is additionally secured with two friction roller catches with metal strike plates.

Hinged glazed doors, 48 inches (1219 mm) or less in height, have a solid 	wood frame 1 1/16 inches (27 mm) by 3 inches (76 mm) with glass panel. 	Doors overlap opening 1/4 inch (6 mm) on all sides. The frame joints are 	bored, doweled and glued. The balance of the door is glass. Right door of 	double doors laps over an applied astragal on left door. Doors have one pull, 	two hinges and are secured by friction roller catches with metal strike plate. 	Glass panels are held in place by a press-fit, flexible and removable, rubber 	strip.

        - Glass is tempered safety glass is specially heat-treated glass, 1/4 inch (6 mm) thick with a minimum of 88 percent clarity.

b.	Glass is DSB glass is double strength, grade “B”, and 1/8 inch (3 mm) 				thick.

3.	Hinged glazed doors, 48 inches (1219 mm) or less in height, have a solid 			wood frame 1-1/16 inches (27 mm) by 3 inches (76 mm) with glass panel. 			The hardwood rail and stile frame joints are bored, doweled and glued. Right 			door of double doors laps an applied astragal on the left door. Doors have 			one pull, two hinges and are secured by friction roller catches with metal 			strike plate. Glass panels are held in place by a press-fit, flexible and 				removable, rubber strip.

a.	Glass is tempered safety glass is specially heat-treated glass, 1/4 inch 				(6 mm) thick with a minimum of 88 percent clarity.

        - Glass is DSB glass is double strength, grade “B”, and 1/8 inch (3 mm) thick.

4	Hinged glazed doors, over 48 inches (1219 mm) in height, same construction 	with a 1-1/16 inch (27 mm) by 3 inch (76 mm) center cross frame member 	with glass panel. Single doors and right door of double doors have a latching 	handle. Left door of double doors has a fixed handle, which is the same size 	and finish as a latching handle. A three point latching system provides single 	doors and right door of double doors positive engagement at the top and 	bottom of the door with tapered aluminum rods, which engage plastic, strike 	plates and pulls the door snug. The rods are 5/16-inch (8 mm) in diameter 	and move in nylon guides attached to the back of the door. The middle of the 	door is secured by a latch plate, which engages the side of the case, or 	latches behind the left door on cases with double doors and securely hold the 	door shut. Right door of double doors laps an applied astragal on the left 	door. Doors have four hinges. The left door of double doors is additionally 	secured by two friction roller catches and metal strike plates. Glass panels 	are held in place by a press-fit, flexible and removable, rubber strip.

        - Glass is tempered safety glass is specially heat-treated glass, 1/4 inch (6 mm) thick with a minimum of 88 percent clarity.

        - Glass is DSB glass is double strength, grade “B”, and 1/8 inch (3 mm) thick.

J.	Construction - Sliding Doors:

      - Sliding solid doors are 3/4 inch (19 mm) thick with squared edges; and operate in an overhead aluminum sliding door track assembly with adjustable nylon roller hangers.  Doors are secured at the bottom of the cabinet with two plastic guides per door that operate in recessed, channels. Each door has one recessed pull with finger grip. Pull is located on outside edge of the door face.  Lock is furnished when specified.

      - Sliding glazed doors, 48 inches (1219 mm) or less in height, have a 1 1/16 inches (27 mm) by 3 inches (76 mm), solid wood frame with 1/8 inch (3 mm) thick DSB glass. Plastic laminate sliding glazed doors are 3/4 inch (19 mm), laminate on particleboard core. Door frames have joints bored, doweled and glued. The balance of the door is glass. Doors operate in an overhead aluminum sliding door track assembly with adjustable nylon roller hangers.  Doors are secured at the bottom of the cabinet with two plastic guides per door, which operate in recessed channels.  Each door has one pull recessed nickel-plated metal pull with finger grip. Pull is located on outside edge of the door face. Lock is furnished when specified.

        - Glass is tempered safety glass is specially heat-treated glass, 1/4 inch (6 mm) thick with a minimum of 88 percent clarity.

        - Glass is DSB glass is double strength, grade “B”, and 1/8 inch (3 mm) thick.

      - Sliding glazed doors, over 48 inches (1219 mm), have a 1 1/16 inches (27 mm) by 3 inches (76 mm), solid wood frame with a center cross frame member and 1/4 inch (6 mm) tempered glass. Doors have solid wood frames with joints bored, doweled and glued. The balance of the door is glass. Doors operate in an overhead aluminum sliding door track assembly with adjustable nylon roller hangers.  Doors are secured at the bottom of the cabinet with two plastic guides per door, which operate in recessed channels. Each door has one recessed nickel-plated metal pull with finger grip. Pull is located on outside edge of the door face. Lock is furnished when specified. Glass is tempered safety glass is specially heat-treated glass, 1/4 inch (6 mm) thick with a minimum of 88 percent clarity.

      - Sliding glass doors are 1/4 inch (6 mm) thick float glass. Doors have polished vertical edges and swiped horizontal edges. Doors operate in sliding aluminum door track assembly, which has an aluminum track at the bottom, and an aluminum channel mounted at the top of the cabinet. The glass rests in aluminum shoes with nylon rollers. The top swiped edge of the glass is fitted with plastic glide clips to assure smooth movement in the channel.  Each door has one two-piece recessed round pull.  Pull is located on outside edge of the door face.  Lock is furnished when specified.

K.	Construction - Tables: Open Frame Table exterior rails are 4-13/16 inches (122 mm) 		by 13/16 inch (21 mm), solid hardwood lumber. Interior rails are a minimum of 3/4 		inch (19 mm) hardwood plywood. Compartment bottoms are 1/4 inch (6 mm) 			plywood. Legs are 2 1/4 inches (57 mm) square solid hardwood; legs are not laid 		up. Leg stretchers, when specified, are 2-1/8 inches (54 mm) by 1 inch (25 mm) 		thick, solid hardwood Openings are routed in the one-piece rail when drawers or 		compartments are required. A minimum of two interior cross rails are doweled and 		glued into exterior rails. Compartment bottoms are let into dadoed grooves in cross 		rails and the front and back rails, then glued on all four edges. Exterior rails are 		grooved to receive 3/8 inch (9 mm) flanges on the 13 gauge steel corner stabilizing 		bracket. Legs are secured to the stabilizing bracket with a 5/16 inch (8 mm) 			threaded hanger bolt, machine screwed into the solid leg a depth of at least 1-1/2 		inches. The stabilizing bracket is attached to the leg bolt by a 5/16”locking nut with 		serrated flange. Tightening the locking nut on the bolt, draws the stabilizing bracket 		flanges against the solid hardwood rail, and clamps them against the solid hardwood 		leg. The stabilizing bracket is further secured to the solid hardwood rails by four (4) 		Euro screws. Legs have molded black polyethylene, closed bottom, leg shoes. 		Exterior rails are also grooved to accept Z- clips for attaching the top.

2.6	FlNlSHES

A.	Wood Cabinets: Exterior and interior surfaces of cabinets receive the full finishing 		process consisting of baked on: specified NGR stain, two coats of protective 			moisture resistant sealer and two applications of a topcoat of clear catalyzed 			chemical resistant lacquer.

1.	Interior Surfaces: The unexposed interior surfaces of cupboards, wall cases, 			upper cases, and tall cases must match exterior color and receive stain (color 			coat), a protective coat of moisture resistant sealer, and two applications of a 			clear, catalyzed, chemical resistant lacquer.

2.	Other Surfaces: Unexposed surfaces such as unexposed end panels, 				unexposed backs are processed through standard finishing steps and receive 			a baked on protective coat of moisture resistant sealer, but no stain (color 			coat).

3.	Finish shall comply with SEFA-8W resistance standard acceptable levels for 			casework surfaces.  An independent 3rd party testing facility's written 				certification must be provided to establish that final finish has no more than 			four, SEFA-8W "Level 3" conditions.

4.	Any deviations from the specified finishing procedures will be considered 			defective Work and rejected by the Architect.

2.7	CABINET HARDWARE

A.	Provide laboratory casework manufacturer's standard finish, commercial-quality, 		heavy-duty hardware complying with requirements indicated for each type.

B.	Lock GL-1 is ratchet type glass door lock, with a disc tumbler mechanism and a 		polished nickel plate finish.  The ratchet bar adjusts from 1 inch (25 mm) to 3 3/8 		inches (86 mm). Two keys are provided; master keying is not available.  Locks are 		furnished only when specified.

C.	Friction roller catch is zinc plated steel catch with a spring cushioned; polyethylene 		roller, and a metal strike plate.  Screw mounted catches and strike plate have slotted 		holes for adjustability.

    - Sliding door track assembly DT-1 has an overhead aluminum track and adjustable, nylon roller hangers.  The lipped edge of the upper aluminum track prevents rollers from jumping track. Two hard plastic guides are mounted on the bottom interior of the door and operate in recessed channels.

    - Sliding glass door track assembly GT-1 has an aluminum bottom track, and an aluminum channel mounted at the top of the cabinet. The glass rests in aluminum shoes with nylon rollers, which operate in the bottom track. The top swiped edge of the glass is fitted with plastic glide clips to assure smooth movement in the channel.

    - Shelf clips are made from clear polycarbonate and are laboratory standard grade. Clips have double, 3/16 inch (5 mm) diameter pins and are equipped with shelf lock hold down tabs for 3/4 inch (18 mm) or 1 inch (25 mm) thick shelves.

    - Sliding door lock, when specified, 5-disc tumbler mechanism with a dull chrome plated face. Tumblers and keys are brass, while plug and cylinder are die cast steel. Pushing in on the lock while turning the key, engages a lock bolt into the strike plate; a turn of the key, unlocks the bolt. There are 200 key changes standard. Locks are keyed differently, master keyed and furnished with 2 keys per lock. Locks and corresponding keys are alpha-numerically coded for a quick match.

    - Leg shoes are closed-bottom style, 2 1/4 inches (57 mm) square, and molded of 1/8 inch (3 mm) black polyethylene.

2.8	COUNTER TOPS

A.	Chem-Surf exposed surface and edges are horizontal grade, high pressure, plastic 		laminate applied to particleboard core. Finished top is 1 inch (25 mm) thick, and the 		curb is 4 inches (102 mm) high. A phenolic backing sheet is applied to the bottom 		surface. Standard Color:  Black.

B.	Maple top is composed of laminated strips of electronically glued, select hard maple 		in natural finish color. The top surface is finished with two coats of UV cured, 			penetrating acrylic sealer; and, the bottom surface receives one coat.  Standard 		thickness is 1 3/4 inches (44 mm) and the applied curb is four inches (102 mm) high 		and 3/4 inch (19 mm) thick.

C.	Phenolic is a solid resin material composed of laminates of high-pressure thermoset 		plastic. The finished top is 1 inch (25 mm) thick, and the curb is 4 inches (102 mm) 		high. Color:  Black with a black core.

D.	Epoxy resin (Rhearesin) is 1 inch (25 mm) thick, molded from a modified epoxy 		resin. Exposed edges and corners are radiused, and a drip groove is provided under 		surface in areas where sinks are installed.  Curb is 4 inches (102 mm) high. Color:  		Black.

E.	Sandstone (Rhearock) is natural quarried sandstone, free of veins, laminations and 		stratifications, is first impregnated with a highly chemical resistant polymerizing 		resin.  A 5 mil thick (four base coats and three finish coats), chemical resistant 			resinous coating is then applied to exposed surfaces. The impregnating resin and 		surface coatings are heat polymerized to cure the resin, toughen the stone, and 		provide a chemical and heat resistant, uniform surface.  Exposed edges and corners 		are radiused, and a drip groove is provided on the under surface, when specified. 		Top is one inch thick, and the curb is 4 inches (102 mm) high. Color:  Black.

F.	Rheatex exposed surface and edges are horizontal grade, high pressure, plastic 		laminate applied to particleboard core. Finished top is 1 inch (25 mm) thick, and the 		curb is 4 inches (102 mm) high.  A phenolic backing sheet is applied to the bottom 		surface. Color:  Black.

G.	Stainless Steel top is fabricated from 16 gauge stainless steel, and exposed 			surfaces have a No. 4 satin finish. The sink is reinforced on the full length of the 		underside with number 16-gauge steel, U-type, structural channels. A wood or steel 		frame, around the front and ends, is provided for fastening to cabinet. Sink bowls 		are seamless, electrically welded, and ground and polished to a hand blended satin 		finish. Drain boards, flanges, curbs and back splashes are integral. Joints are 			electrically welded, then ground and polished to a hand blended satin finish. The 		entire unit is sound deadened.

H.	Tuf-Surf exposed surface and edges are horizontal grade, extra-high wear resistant, 		high pressure plastic laminate.  The laminate is bonded to particleboard core. The 		finished top is 1 inch (25 mm) thick, and the curb is 4 inches (102 mm) high. Color:  		Black with matte, textured finish.

2.9	ACCESSORIES:

A.	Burette Rods:  1/2 inch (12 mm) diameter, anodized aluminum, and either 18 inches 		(457 mm) or 24 inches (610 mm)long.  Rods are furnished with a tapered aluminum 		adapter to fit rod socket.

B.	Clamps:  1 inch (25 mm) square aluminum stock, with two, 3/4 inch (19 mm) 			diameter openings, at right angles to each other, bored   through sides. Openings 		are for upright rods and crossbars, or Greenlaw Arms. Thumb screw into each end 		of the clamp; tighten against the rods to hold positions.

C.	Crossbars and Greenlaw Arms: 3/4 inch (19 mm) diameter, anodized aluminum 		rods, with ends rounded.

D.	Rod Sockets:  Mushroom type, machined from a solid aluminum rod.  Sockets are 		held in place by a heavy aluminum lock nut and washer.

E.	Upright Rods:  3/4 inch (19 mm) diameter, anodized aluminum, 36 inches long with 		a rounded top and a tapered bottom to fit rod sockets.

F.	Reagent Shelves:  Provide as indicated, fabricated from same material as adjacent 		countertop, unless otherwise indicated.

G.	Adjustable Wall Shelf Supports: Standard is anodized chrome standard and shelf 		brackets. Epoxy powder coating is an option and must be specified.

H.	Metal Key Cabinets.

    - Plastic Tote Tray.

    - Pegboards:	Clear acrylic, epoxy, or phenolic-composite pegboards with removable polypropylene pegs and stainless-steel drip troughs with drain outlet.

2.10	SERVICE FIXTURES

A.	Electrical Components, Devices, and Accessories shall be labeled to comply with 		NFPA 70, Article 100 and marked for its intended use.

B.	Provide service fixtures and fittings that comply with SEFA 7.

      - Provide service fixtures and fittings that comply with recommendations of SEFA 7.

C.	Electrical Fixtures are 3-wire grounded, 20 A, 125V AC, with stainless steel cover 		plates and cadmium-plated steel boxes.  Pedestal boxes are black, cast aluminum 		with conduit nipples and lock nuts.  When specified, G.F.C.I., ground fault circuit 		interrupter fixtures are available. G.F.C.I. fixtures are 20 A, 125V AC, with black 		nylon faceplate.

      - Receptacles:  Comply with NEMA WD 1, NEMA WD 6, FS W-C-596, and UL 498.  Duplex type, Configuration 5 20R.

D.	Epoxy resin sinks are drop-in style, non-glaring black, and specially modified epoxy 		resins, molded in one solid piece or optimum physical and chemical resistance. 		Inside corners are coved and the bottom is dished to the outlet. Outlets are 			polypropylene with 1 1/2 inch (38 mm) NPS threads.

E.	Gas, Air and Vacuum Cocks:  Ground key cocks, made from high grade, brass 		forgings, have integral ten serration, non-slip hose end. Wing or knob handle has 		color-coded index, is one-piece construction, precision ground, and lapped to fit 		cock chamber. Handle operates with a 1/4 turn, and is spring-loaded for constant 		pressure and automatic take up. Provide needlepoint valves for high pressures and 		oxygen service where scheduled.

F.	Multiple Service Fixtures: Triple chrome plated or electro-statically applied polyester 		powder coated fixtures have one cold water faucet and two ground key cocks for 		gas, air, or vacuum services.   Faucet has a rigid gooseneck, one four-arm or knob 		handle, and serrated hose nozzle. Vacuum breaker furnished when specified.  			Faucet with integral vacuum beaker is furnished, when specified. Ground key cocks 		have serrated non-slip hose end and color-coded, spring-loaded wing handles.

G.	Service Fixtures: Triple chrome plating or electro-statically applied polyester powder 		coating, heavy-duty construction for water, gas, steam, or other services and 			specifically designed for laboratory use.  Hot and/or cold Water Faucets are cast 		from red brass with color-coded index handles. Faucets have serrated hose nozzles, 		unless specified otherwise. Goosenecks are rigid.  Fixture outlets are tapped 3/8-		inch (10 mm) I.P.S. for aerators, vacuum breakers, hose connections, or other 			accessories. Faucets with an integral vacuum breaker.

H.	Stainless steel sinks have a satin finish. Sink is 18 gauge, type 304, 18-8 stainless 		steel, with heavily undercoated bottoms and positive pitch drains. Outlets are 			chrome-plated brass. Drain holes are 3 1/2 inches (89 mm) diameter for 4 1/2 			inches (114 mm) stainless steel cup strainers. The cup strainer has a neoprene 		stopper.

I.	Vacuum Breakers:  Watts NLF-9, or comparable, vacuum breakers are brass with 		polished chrome plating, screw-in type with stainless steel working parts, and 			durable rubber diaphragm and disc. Vacuum breaker is for hot or cold faucet and 		has a primary valve with a soft disc that seat against mating part. The secondary 		check valve utilizes a soft disc to metal seating.  Breaker is tapped 3/8-inch (10 mm) 		N.P.T.  Vacuum breaker is not intended for constant high pressures. Vacuum 			breakers shall be furnished where scheduled.

2.11	EQUIPMENT AND APPLIANCES

A.	Flammable Liquid Storage Cabinets: Provide units that comply with requirements of 		NFPA 30.

1.	Wood, UL rated cabinet.

2.12	FUME HOODS	Please refer to ICI Fume Hood Specifications for options.

PART 3  EXECUTION

3.1	EXAMINATION

A.	Do not begin installation until substrates have been properly prepared.

1.	Walls and openings are plumb, straight and square.

      - Concrete floors level within 1/8 inch (3 mm) level per 10 foot (3000 mm) run, non-accumulative, when tested with a straight edge in any one direction.

B.	If substrate preparation is the responsibility of another installer, notify Architect of 		unsatisfactory preparation before proceeding.

3.2	COORDINATION

A.	Laboratory equipment contractor shall furnish equipment to the building, setting in 		place, leveling and scribing to walls and floors. Furnish plumbing and electrical 		fixtures, including nipples and lock nuts needed to secure each fixture to the 			equipment.

B.	Coordination with mechanical contractor who shall furnish, install and connect drain 		lines, service piping, vents, re-vents, in-line vacuum breakers, special plumbing 		fixtures, traps and tailpieces.  Work to be completed through, under or along backs 		of working surfaces as required and complete final connection of services. 			Assemble, install and make final connections of service fixtures furnished by 			casework contractor, including service fixtures in fume hoods. Furnish, install and 		connect fume hood blowers, motors and all related ductwork. Furnish, install and 		connect service piping within fume hoods, including final connection.

C.	Coordination with electrical contractor who shall furnish, install and connect 			electrical service lines, wire and conduit within the equipment, including reagent 		racks and fume hoods. Work to be completed through, under or along backs of 		working surfaces as required and complete final connection of services. Install and 		make final connections of electrical fixtures provided by casework installer, including 		electrical fixtures in fume hoods.

3.3	PREPARATION

A.	Clean surfaces thoroughly prior to installation.

B.	Prepare surfaces using the methods recommended by the manufacturer for 		achieving the best result for the substrate under the project conditions.

3.4	INSTALLATION

A.	Install casework in accordance with manufacturer's instructions.

1.	Installation of casework shall be plumb, level, true and straight, with no 				distortions.

2.	Use concealed shims as required.

      - Where laboratory casework or equipment butts against other finished work, scribe and cut for an accurate fit.

      - Lubricate operating hardware as recommended by the manufacturer.

B.	Install countertop and edge surfaces in one plane with flush hairline seams.  Locate 		seams where shown on Shop Drawings.

1.	Provide required holes and cutouts for service fittings as shown on Shop 			Drawings.

2.	Seal unfinished edges and cutouts in plastic-laminate countertops.

3.	Provide scribe moldings for closures at junctures of countertop, curb, and 			splash, with walls as recommended by manufacturer for materials involved.  			Match materials and finish to adjacent laboratory casework.  Use chemical-			resistant, permanently elastic sealing compound where recommended by 			manufacturer.

4.	Carefully dress joints smooth, remove surface scratches, and clean entire 			surface.

C.	Coordination with Mechanical, Plumbing and Electrical Contractors: Coordinate work 		of this Section with work of other Sections including but not limited to:

1.	Water and laboratory gas service fittings, piping, electrical devices, and 				wiring.

2.	Installation of fittings according to Shop Drawings and manufacturer's written 			instructions.

3.	Setting bases and flanges of sink and countertop-mounted fittings in sealant 			recommended by manufacturer of sink or countertop material.

4.	Anchorage of fittings, piping, and conduit to laboratory casework, unless 			otherwise indicated.

3.5	PROTECTION

A.	Cover installed casework and equipment with 4-mil polyethylene.

B.	Protect installed products until completion of project.

C.	Touch-up, repair or replace damaged products before Substantial Completion.

D.	A qualified manufacturer representative shall demonstrate operation and 			maintenance procedures of the installed casework and equipment to the Owners 		personnel.

END OF SECTION