## NG Pressure Drop - LP
NATURAL GAS PIPE PRESSURE DROP CALCULATION
Client: |  | BP |  |  |  |  | Calculated By: | NPZ
Project: |  | Whiting Firehouse & Security Building |  |  |  |  | Date: | 2013-06-12
Project Number: |  | RUS - 00211408-A2
Building NG Piping Parameters |  |  |  |  | Schedule 40 Steel Pipe Standard Sizes2
Total Developed Load (CFH): |  | 2160 | CFH |  | Nominal Size (inches) | Internal Diameter (Inches) | Nominal Size (inches) | Internal Diameter (Inches)
Total Developed Distance: |  | 150 | Feet
Inlet Pressure: |  | <2 | psi
Estimated Pressure Drop: |  | 0.5 | Inches of W.C. |  | 0.25 | 0.364 | 1.5 | 1.61
Specific Gravity: |  | 0.6 |  |  | 0.375 | 0.493 | 2 | 2.067
Piping Type: |  | Schedule 40 Metalic Pipe |  |  | 0.5 | 0.622 | 2.5 | 2.469
Incoming Pressure at Meter: |  | 27.7 | Inches of W.C. |  | 0.75 | 0.824 | 3 | 3.068
Total System Pressure Drop:1 |  | 0.26127 | Inches of W.C. |  | 1 | 1.049 | 3.5 | 3.548
Pressure at Furthest Point: |  | 27.4387 | Inches of W.C. |  | 1.25 | 1.38 | 4 | 4.026
Segment | Piping Length (feet) | Nominal Size (inches) | Internal Diameter (Inches) | NG Flow (CFH) | Pressure Drop (inches of WC)1
1 | 67 | 3 | 3.068 | 2160 | 0.15563
2 | 83 | 3 | 3.068 | 1560 | 0.10565
3 | 0 | 1 | 1.049 |  | 0
4 | 0 | 1 | 1.049 |  | 0
5 | 0 | 1 | 1.049 |  | 0
6 | 0 | 1 | 1.049 |  | 0
7 | 0 | 1 | 1.049 |  | 0
8 | 0 | 1 | 1.049 |  | 0
9 | 0 | 1 | 1.049 |  | 0
10 | 0 | 1 | 1.049 |  | 0
11 | 0 | 1 | 1.049 |  | 0
12 | 0 | 1 | 1.049 |  | 0
13 | 0 | 1 | 1.049 |  | 0
14 | 0 | 1 | 1.049 |  | 0
15 | 0 | 1 | 1.049 |  | 0
16 | 0 | 1 | 1.049 |  | 0
TOTAL | 150 | 3 | 3.068 | 2160 | 0.26127
Notes: | 1: The pressure drop equation used is from the 2006 IFGC, (Section 402.4, Equation 4-1). This eqation applies to low pressure applications (less than 1.5 psi).
2: The table used is from the 2006 IFGC, (Appendix A, Section A.5, Table A.5.1).

## NG Pressure Drop - HP
NATURAL GAS PIPE PRESSURE DROP CALCULATION
Client: | [6 empty] | Calculated By:
Project: | [6 empty] | Date:
Project Number:
Building NG Piping Parameters |  |  |  |  | Schedule 40 Steel Pipe Standard Sizes2
Total Developed Load (CFH): |  | 2160 | CFH |  | Nominal Size (inches) | Internal Diameter (Inches) | Nominal Size (inches) | Internal Diameter (Inches)
Total Developed Distance: |  | 150 | Feet
Inlet Pressure: |  | 5 | psi
Estimated Pressure Drop: |  | 0.67696 | psi |  | 0.25 | 0.364 | 1.5 | 1.61
Specific Gravity: |  | 0.6 |  |  | 0.375 | 0.493 | 2 | 2.067
Piping Type: |  | Schedule 40 Metalic Pipe |  |  | 0.5 | 0.622 | 2.5 | 2.469
Pressure at Outlet of Gas Meter: |  | 5 | psia |  | 0.75 | 0.824 | 3 | 3.068
Total System Pressure Drop:1 |  | 0.67696 | psi |  | 1 | 1.049 | 3.5 | 3.548
Pressure at Furthest Point: |  | 4.323 | psi |  | 1.25 | 1.38 | 4 | 4.026
|  | 119.7481 | Inches of W.C.
Segment | Piping Length (feet) | Nominal Size (inches) | Internal Diameter (Inches) | NG Flow (CFH) | Final Pressure (psia)1 | Pressure Drop (psi)
1 | 67 | 1.5 | 1.61 | 2160 | 4.6087 | 0.3913
2 | 83 | 1.5 | 1.61 | 1560 | 4.323 | 0.28566
3 | 0 | 1 | 1.049 |  | 4.323 | 0
4 | 0 | 1 | 1.049 |  | 4.323 | 0
5 | 0 | 1 | 1.049 |  | 4.323 | 0
6 | 0 | 1 | 1.049 |  | 4.323 | 0
7 | 0 | 1 | 1.049 |  | 4.323 | 0
8 | 0 | 1 | 1.049 |  | 4.323 | 0
9 | 0 | 1 | 1.049 |  | 4.323 | 0
10 | 0 | 1 | 1.049 |  | 4.323 | 0
11 | 0 | 1 | 1.049 |  | 4.323 | 0
12 | 0 | 1 | 1.049 |  | 4.323 | 0
13 | 0 | 1 | 1.049 |  | 4.323 | 0
14 | 0 | 1 | 1.049 |  | 4.323 | 0
15 | 0 | 1 | 1.049 |  | 4.323 | 0
16 | 0 | 1 | 1.049 |  | 4.323 | 0
TOTAL | 150 | 1.5 | 1.61 | 2160 | 4.323 | 0.67696
Notes: | 1: The pressure drop equation used is from the 2006 IFGC, (Section 402.4, Equation 4-2). This eqation applies to high pressure applications (greater than 1.5 psi).
2: The table used is from the 2006 IFGC, (Appendix A, Section A.5, Table A.5.1).

## Sheet 3
Natural gas pressure drop calculation for BP WBU FIREHOUSE & SECURITY BUILDING Project
Length in ft | pipe dia | flow cfh | differential pressure in inch of WC
67 | 3 | 2160 | 0.17163
83 | 3 | 1560 | 0.11649
0 | 1 | 0 | 0
0 | 1 | 0 | 0
0 | 1 | 0 | 0
0 | 1 | 0 | 0
0 | 1 | 0 | 0
| Total pressure drop |  | 0.28811 | inches of WC
Incoming pressure at meter |  |  |  | 27.7 | inches of WC
Pressure drop at farthest point |  |  |  | 27.4119 | inches of WC