## SI
SWIMMING POOL
DEHUMIDIFICATION CALC
305 Sport Activity Building
Pool evaporation
Wp = 4 E-5 A (pw - pa) Fa
Reference: 2011 Ashrae Handbook Applications 5.6
Water temperature (C) | 27
Air temperature (C) | 28
Relative humidity (%) | 50
A: area of pool surface (m2) | 325
pw: saturation vapor pressure taken at surface water temperature, kPa | 3.5679
pa: saturation pressure at dew point, kPa | 1.8925
Fa: activity factor | 1
Wp: evaporation of water (kg/s) | 0.02178
Wp: evaporation of water (kg/h) | 78.4087

## IMPERIAL
SWIMMING POOL
DEHUMIDIFICATION CALC
305 Sport Activity Building
Pool evaporation
Wp = 0.1A (pw - pa) Fa
Reference: 2015 Ashrae Handbook Applications 5.6
Water temperature (f) | 80.6
Air temperature (f) | 82.4
Relative humidity (%) | 50
A: area of pool surface (ft2) | 3497
pw: saturation vapor pressure taken at surface water temperature, In.Hg | 1.0546
pa: saturation pressure at dew point, In.Hg | 0.55844
Fa: activity factor | 1
Wp: evaporation of water (lb/hr) | 173.5072
Wp: evaporation of water (lb/s) | 0.048196
80.6
0.518 | psia
1.0546 | In.Hg