## Generators
Design calculation sheet
Project no: |  |  | Date: |  | Sheet no.: | 1 | 1 | Computed by:
Subject: | Generator Room | [6 empty] | Checked by:
| Louvers Sizing | [6 empty] | Approved by:
| Generator : |  | Cummins |  | Model : | Caterpillar |  |  | 1000 | kVA
kw = kVA x cosΦ
| Number of Generators : |  |  | 1 | Active + | 0 | Stand by |  | cosΦ = 0.8
Radiator Fan "ON" when Generator "OFF" for Cooling
| Design Temperature |  |  |  | Maximum Allowable Room Temp. |  |  | Resulting Allowable ⌂T
| 104 | ºf |  | 122 | ºf |  |  |  | = | 18
Heat Rejected to Ambient by 1 generator when running:
|  |  | Engine Dissipation | = | 717188 | Btu/hr
|  |  | Generator Dissipation | = |  | Btu/hr |  | Total = | 717188 | Btu/hr
per generator
Ventilation Requirements to prevent temperature rise above recommended limit
| cfm | = | Q |  | = | 717188 |  | = | 36893 | cfm
|  |  | 1.08 | x ⌂T |  | 1.08 | 18 |  | 17411 | lps
per generator
Air Flow as per catalogue per generator:
|  |  |  | Radiator Cooling Air | = | 100 | cfm
|  |  |  | Combustion air | = |  | cfm
[6 empty] | 100 | cfm | = | 49160 | cfm
| Intake area, is based on |  |  | 1000 | fpm velocity
| Q = A x V => |  | A = | Q | = | 49160 | = | 49.16 | ft2 = | 4.5695 | m2
|  |  |  | V |  | 1000
| Using an Intake Louver Free Area of |  |  |  | 50%
[6 empty] | Gross |  | Net
| Intake Area per Generator: |  |  |  |  | 98.32 | ft2 | 49.16 | ft2
| Total Required Intake Area for |  |  |  |  | Gross |  | Net
| 1 | Operating Generators |  |  |  | 98.32 | ft2 | 49.16 | ft2
| Exhaust area, based on |  |  | 1000 | fpm velocity
| Q = A x V => |  | A = | Q | = | 49160 | = | 49.16 | ft2 = | 4.5695 | m2
|  |  |  | V |  | 1000
| Using an Intake Louver Free Area of |  |  |  | 50%
[6 empty] | Gross |  | Net
| Exhaust Area per Generator |  |  |  |  | 98.32 | ft2 | 49.16 | ft2
Total Required Intake Area for
| 1 | Operating Generators |  |  |  | 98.32 | ft2 | 49.16 | ft2
of

## Transformer
Design calculation sheet
Project no: |  |  | Date: |  | Sheet no.: | 1 | 1 | Computed by:
Subject: | Transformer Room Ventilation | [6 empty] | Checked by:
Approved by:
| Transformer : |  | France Transfo |  | Model : |  |  |  | 1000 | kVA
kw = kVA x cosΦ
| Number of Transformer : |  |  | 1 |  |  |  |  | cosΦ = 0.8
| Design Temperature |  |  |  | Maximum Allowable Room Temp. |  |  | Resulting Allowable ⌂T
| 86 | ºf |  | 104 | ºf |  |  |  | = | 18
| Heat Rejected to Ambient by 1 Transformer: |  |  |  |  | 30 | kW | = | 102360 | Btu/hr
per Transformer
| Total Heat Generation : |  |  | 1 |  | 30 | kw | = | 102360 | Btu/hr
Total
Ventilation Requirements per Transformer
| cfm | = | Q |  | = | 102360 |  | = | 5266 | cfm
|  |  | 1.08 | x ⌂T |  | 1.08 | 18 |  | 2486 | lps
per transformer
| Total Ventilation Requirements per |  |  |  | 1
|  |  |  | 1 | x | 5266 |  | = | 5266 | cfm
[9 empty] | 2486 | lps
Total
| Intake area, is based on |  |  | 200 | fpm velocity
| Q = A x V => |  | A = | Q | = | 5266 | = | 26.4 | ft2 = | 2.5 | m2
|  |  |  | V |  | 200
| Using an Intake Louver Free Area of |  |  |  | 50%
[6 empty] | Gross |  | Net
| Intake Area per Transformer |  |  |  |  | 52.8 | ft2 | 26.4 | ft2
| Total Required Intake Area for |  |  |  |  | Gross |  | Net
| 1 | Operating Transformer |  |  |  | 52.8 | ft2 | 26.4 | ft2
| Exhaust area, based on |  |  | 300 | fpm velocity
| Q = A x V => |  | A = | Q | = | 5266 | = | 17.5533 | ft2 = | 1.6316 | m2
|  |  |  | V |  | 300
| Using an Intake Louver Free Area of |  |  |  | 50%
[6 empty] | Gross |  | Net
| Exhaust Area per Transformer |  |  |  |  | 35.1067 | ft2 | 17.5533 | ft2
Total Required Intake Area for
| 1 | Operating Transformer |  |  |  | 35.1067 | ft2 | 17.5533 | ft2
of

## Data (hidden)
25% | Radiator Fan "ON" when Generator "OFF" for Cooling
30% | Radiator Fan & Generator "OFF" : No cooling
40%
50%
55%
60%
65%
70%
75%