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	Specifications

	Model
	AMAR09HP115V1C

	Indoor Unit
	AMAR09HP115V1CH

	Outdoor Unit
	AMAR09HP115V1CO

	Cooling
	Capacity
	Rated
	Btu/h
	9200 

	
	Capacity Range
	Min-Max
	Btu/h
	1700-13000

	
	Power Input
	Rated
	W
	657 

	
	Operating Range
	                    °F 
	5-125

	Heating
	Capacity at 47F
	Rated
	Btu/h
	10000 

	
	Capacity Range
	Min-Max
	Btu/h
	1700-15700

	
	Power Input at 47F
	Rated
	W
	750 

	
	Capacity at 17F
	Rated
	Btu/h
	11900 

	
	Capacity at 5F
	Max
	Btu/h
	9400 

	
	Capacity at -5°F
	Max
	Btu/h
	7000 

	
	Operating Range
	                    °F 
	-13-75

	Efficiency
	SEER2
	25 

	
	HSPF2
	10.5 

	Indoor Unit
	Air Flow Rate(SH/H/M/L/Q)
	CFM
	355/315/282/255/180

	
	Sound Pressure Level
	Cooling
	dB(A)
	41/36/34/31/26

	
	
	Heating
	dB(A)
	41/36/33/29

	
	Package Dimensions
	H
	In.[mm]
	11-13/16 [300]

	
	
	W
	In.[mm]
	32-7/8 [835]

	
	
	D
	In.[mm]
	14-39/64 [371]

	
	Net Dimensions
	H
	In.[mm]
	8-27/64 [214]

	
	
	W
	In.[mm]
	30-15/32 [774]

	
	
	D
	In.[mm]
	11-13/16 [300]

	
	Net Weight
	Ibs[kg]
	17.7 [8]

	Outdoor Unit
	Package Dimensions
	H
	In.[mm]
	24-7/32 [615]

	
	
	W
	In.[mm]
	35-35/64 [903]

	
	
	D
	In.[mm]
	15-3/64 [382]

	
	Net Dimensions
	H
	In.[mm]
	21-59/64 [557]

	
	
	W
	In.[mm]
	34-41/64 [880]

	
	
	D
	In.[mm]
	13-57/64 [353]

	
	Net Weight
	Ibs[kg]
	67.2 [30.5]

	
	Sound Pressure Level
	Cooling
	dB(A)
	53 

	
	
	Heating
	dB(A)
	53 

	Piping
	Diameter
	Gas(0.D.)
	In.[mm]
	3/8 [9.52]

	
	
	Liquid(0.D)
	In.[mm]
	1/4 [6.35]

	
	
	Indoor Drain
	In.[mm]
	5/8 [15.88]

	
	Min.Length
	ft [m]
	9 [2.74]

	
	Max.Length
	ft [m]
	65 [20]

	
	Max.Height
	ft [m]
	50 [15]

	Electrical
	Outdoor-Indoor
	V,ph,Hz
	115,1,60

	
	Recommended Breaker Size
	A
	25 

	
	MCA
	A
	20 

	
	MOCP
	A
	25 

	Refrigerant 
	Refrigerant Type
	R32

	
	Pre-Charge Amount oz
	29.63

	
	Additional Charge Per Foot over 25ft
	0.172oz/ft


Remarks:
1.All specifications are subject to change by the manufacturer without prior notice.
2.All units are being tested and comply to ISO5151.
3.Sound pressure levels are measured in anechoic chamber.
  During actual operation, sound pressure level will be higher as a result of room specification condition.
4.Data from AUX lab,05/03/24, Data may change according to test surroundings, AUX reserves right of explanation on data.
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Dimensions
Indoor Unit: 
AMAR09HP115V1CH
[image: /Users/caesar/Desktop/奥克斯美国/资料/1130/C-Series Drawing/Indoor Unit - 102224/indoor unit/26CD.png26CD]
[image: /Users/caesar/Desktop/奥克斯美国/资料/1130/C-Series Drawing/Indoor Unit - 102224/美自品安装图-CSeries内机.png美自品安装图-CSeries内机]

	
Dimensions
Outdoor Unit: 
AMAR09HP115V1CO
[image: /Users/caesar/Desktop/奥克斯美国/资料/1130/C-Series Drawing/Outdoor Unit -241120/1.8PA/1.8PA美国自品外机(家用).png1.8PA美国自品外机(家用)]













Clearances 
Outdoor Unit: 
AMAR09HP115V1CO
[image: /Users/caesar/Desktop/奥克斯美国/资料/1130/C-Series Drawing/Outdoor Unit -241120/1.8PA/1.8PA美国自品外机(家用)-安装图.png1.8PA美国自品外机(家用)-安装图] 
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