SUBMITTAL DATA SHEET

AUX R32 – C-Series - AMAR24HP230V1C

| Job Name | Location Date |
| --- | --- |
| Purchaser | Engineer |
| Submitted to | For □Reference □Approval □Construction |
| Unit Designation | Schedule # |

AMAR24HP230V1C

- AHRI No: 214290024

| Specifications |  |  |  |  |
| --- | --- | --- | --- | --- |
| Model |  |  |  | AMAR24HP230V1C |
| Indoor Unit |  |  |  | AMAR24HP230V1CH |
| Outdoor Unit |  |  |  | AMAR24HP230V1CO |
| Cooling | Capacity | Rated | Btu/h | 22500 |
|  | Capacity Range | Min-Max | Btu/h | 4300-28500 |
|  | Power Input | Rated | W | 1610 |
|  | Operating Range | °F |  | 5-125 |
| Heating | Capacity at 47F | Rated | Btu/h | 24000 |
|  | Capacity Range | Min-Max | Btu/h | 5300-31000 |
|  | Power Input at 47F | Rated | W | 1750 |
|  | Capacity at 17F | Rated | Btu/h | 22400 |
|  | Capacity at 5F | Max | Btu/h | 21500 |
|  | Capacity at -5°F | Max | Btu/h | 14300 |
|  | Operating Range | °F |  | -13-75 |
| Efficiency | SEER2 |  |  | 25 |
|  | HSPF2 |  |  | 10.5 |
| Indoor Unit | Air Flow Rate(SH/H/M/L/Q) |  | CFM | 940/833/742/636 |
|  | Sound Pressure Level | Cooling | dB(A) | 51/48/44/39/34 |
|  |  | Heating | dB(A) | 50/48/43/39 |
|  | Package Dimensions | H | In.[mm] | 13-31/32 [355] |
|  |  | W | In.[mm] | 52-3/4 [1340] |
|  |  | D | In.[mm] | 17-33/64 [445] |
|  | Net Dimensions | H | In.[mm] | 10-1/8 [257] |
|  |  | W | In.[mm] | 48-21/32 [1236] |
|  |  | D | In.[mm] | 14-1/16 [357] |
|  | Net Weight | Ibs[kg] |  | 35.3 [16] |
| Outdoor Unit | Package Dimensions | H | In.[mm] | 30 [762] |
|  |  | W | In.[mm] | 39-61/64 [1015] |
|  |  | D | In.[mm] | 16-47/64 [425] |
|  | Net Dimensions | H | In.[mm] | 27-9/16 [700] |
|  |  | W | In.[mm] | 38-37/64 [980] |
|  |  | D | In.[mm] | 15-9/32 [388] |
|  | Net Weight | Ibs[kg] |  | 101.4 [46] |
|  | Sound Pressure Level | Cooling | dB(A) | 59 |
|  |  | Heating | dB(A) | 59 |
| Piping | Diameter | Gas(0.D.) | In.[mm] | 5/8 [15.88] |
|  |  | Liquid(0.D) | In.[mm] | 1/4 [6.35] |
|  |  | Indoor Drain | In.[mm] | 5/8 [15.88] |
|  | Min.Length | ft [m] |  | 9 [2.74] |
|  | Max.Length | ft [m] |  | 100 [30] |
|  | Max.Height | ft [m] |  | 65 [20] |
| Electrical | Outdoor-Indoor | V,ph,Hz |  | 208/230,1,60 |
|  | Recommended Breaker Size | A |  | 25 |
|  | MCA | A |  | 15 |
|  | MOCP | A |  | 25 |
| Refrigerant | Refrigerant Type |  |  | R32 |
|  | Pre-Charge Amount |  |  | 47.6 Oz |
|  | Additional Charge Per Foot over 25ft |  |  | 0.258oz/ft |

Remarks:

1.All specifications are subject to change by the manufacturer without prior notice.

2.All units are being tested and comply to ISO5151.

3.Sound pressure levels are measured in anechoic chamber.

During actual operation, sound pressure level will be higher as a result of room specification condition.

4.Data from AUX lab,05/03/24, Data may change according to test surroundings, AUX reserves right of explanation on data.

Dimensions

Indoor Unit:

AMAR24HP230V1CH

Dimensions

Outdoor Unit:

AMAR24HP230V1CO

Clearances

Outdoor Unit:

AMAR24HP230V1CO